## Copyright Permission
© Biomass Wizard
These Excel spreadsheets have been produced by Gary Battell (Suffolk County Council) with some background data from the Austrian Energy Agency. The sole purpose of these spreadsheets is to freely give away datasets that will improve the quality of information available to the biomass industry. Please credit any use of these tables: Data from the Suffolk County Council Biomass Wizard. We hope you find the information of use?
Information contained within these spreadsheets should be treated as a guide only
Suffolk County Council
Gary Battell - Woodland & Woodfuel Advisor
gjb@afiweb.net - Tel: 01473 264 776 - Mobile: 0750 146 38 32

## Gary Battell
Gary Battell is employed as Woodland Advisor by Suffolk County Council where he works closely with partners such as boiler supplier/installer companies, the Forestry Commission, the CLA, FWAG, Wildlife Trusts, local & national conservation groups and local businesses such as farming cooperatives, land & forestry agents, woodland owners and wood processing business owners.
Gary has 37 years forestry experience and 13 years extensive practical experience within the biomass industry. He along with Alan Tong and Peter Brown were the initial champions for biomass use at Suffolk County Council.
Gary worked with Robert Rippengal and Clarke Willis to set up Anglia Woodfuels Ltd, a successful wood chipping and woodfuel advisory cooperative that operates throughout the East of England.
As a result of Suffolk County Council’s commitment to biomass, Eastern Woodfuels, a new Suffolk business was set up by Sarah Brown and her family at Bentwaters Parks to supply Suffolk County Council with woodfuel. Gary Battell advises them on the wood supply chain, chipping, storage and woodfuel quality. Eastern Woodfuel has provided Suffolk County Council with consistent excellent quality woodfuel and their delivery service has also matched their fuel quality.
Suffolk County Council has offered advice to numerous Local Authorities across the UK, private individuals, businesses and charities , the South Korean and Isle of Man Governments who are considering or have installed biomass boilers and set-up supply chains.
Gary is also a Director and Vice Chairperson of the national Small Woods Association, and director of Heartwoods, advisor to Eastern Woodfuels and sits on the Executive and Steering committees of Woodfuel East.
Gary is also a Steering Group and Partnership member of the national England Woodland and Timber Partnership (EWTP) and Confor (Confederation of Forest Industries - Eastern region).
Gary was joint founder with Ted Green OBE of the Ancient Tree Forum and has done much to promote the care and management of ancient trees along with highlighting the increasing threats from tree pests, pathogens and diseases such as Acute Oak Decline (AOD).
Gary also sits on the Regional Deer Forum and The Wild Venison Project steering and Executive groups.
Gary is also an accomplished speaker and writer on woodlands and woodfuel and is the creator of the Woodfuel Wizard, he cares about one planet living and using our natural resources in a sustainable way which is why he has made the Woodfuel Wizard available free of charge to enhance and expand the biomass industry. Gary is currently producing a Biomass Education Resource Pack that promotes the biomass industry and careers for young people who might want to enter into a forestry/biomass career and he is also writing a book on Staverton, Suffolk. Gary is a Fellow of The Royal Geographical Society. Gary has always given all fees and donations to environmetal charities and claims no expenses for his out of work activities.
Suffolk County Council share their biomass
experience with the South Korean Government.

## Boiler Specification
© Biomass Wizard
Boiler Specification - Performance - Fuel Use
CW Chip P30 M30 & Pellets |  |  |  | Boiler Specifications | [9 empty] | NCW Chip P30 M30 & Pellets |  |  |  | Boiler Specifications | [9 empty] | Pellets |  |  |  | Boiler Specifications | [9 empty] | Pellets |  |  |  | Boiler Specifications
APPROX. BOILER SPECIFICATIONS |  |  |  | CW WOODCHIP | [9 empty] | APPROX. BOILER SPECIFICATIONS |  |  |  | NCH WOODCHIP | [9 empty] | APPROX. BOILER SPECIFICATIONS |  |  |  | Wood Pellets | [9 empty] | APPROX. BOILER SPECIFICATIONS |  |  |  | Miscanthus Pellets
Boiler size | Boiler room | Boiler weight | Water | Boiler size | kWh | P/energy/demand | Full Load | Annual boiler eff. | F/energy/output | tonnes | M3/Yr | 1/wk/Winter | 1 wk winter | Boiler size | Boiler room | Boiler weight | Water | Boiler size | kWh | P/energy/demand | Full Load | Annual boiler eff. | F/energy/output | tonnes | M3/Yr | 1/wk/Winter | 1 wk winter | Boiler size | Boiler room | Boiler weight | Water | Boiler size | kWh | Primary | Full Load | Annual boiler eff. | F/energy/output | tonnes | M3/Yr | 1/wk/Winter | 1 wk winter | Boiler size | Boiler room | Boiler weight | Water | Boiler size | kWh | Primary | Full Load | Annual boiler eff. | F/energy/output | tonnes | M3/Yr | 1/wk/Winter | 1 wk winter
kW | LxWxH | Tonnes | Litres | kW | kg |  | Equivalent Hours | % |  | year | m3 | Tonnes | m3 | kW | LxWxH | Tonnes | Litres | kW | kg |  | Equivalent Hours | % | FLOH - Med | year | M3 | Tonnes | M3 | kW | LxWxH | Tonnes | Litres | kW | kg | Energy Demand | Equivalent Hours | % |  | year | m3 | Tonnes | m3 | kW | LxWxH | Tonnes | Litres | kW | kg | Energy Demand | Equivalent Hours | % |  | year | m3 | Tonnes | m3
15 | 2.5x2.5x2 | 0.669 | 85 | 150 | 3.49 | 338709.6774 | 2100 | 93% | 315000 | 97.0515 | 431.34 | 2.6959 | 11.99 | 15 | 2.5x2.5x2 | 0.669 | 85 | 150 | 3.3 | 338709.6774 | 2100 | 93% | 315000 | 102.6393 | 314.85 | 2.8511 | 8.75 | 15 | 2.5x2.5x2 | 0.669 | 85 | 150 | 4.68 | 338709.6774 | 2100 | 93% | 315000 | 72.3739 | 108.51 | 2.0104 | 3.02 | 15 | 2.5x2.5x2 | 0.669 | 85 | 0 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | 2.5x2.5x2 | 0.695 | 100 | 20 | 3.49 | 45161.2903 | 2100 | 93% | 42000 | 12.9402 | 57.52 | 0.35945 | 1.6 | 20 | 2.5x2.5x2 | 0.695 | 100 | 20 | 3.3 | 45161.2903 | 2100 | 93% | 42000 | 13.6852 | 41.98 | 0.38015 | 1.17 | 20 | 2.5x2.5x2 | 0.695 | 100 | 20 | 4.68 | 45161.2903 | 2100 | 93% | 42000 | 9.6498 | 14.47 | 0.26805 | 0.41 | 20 | 2.5x2.5x2 | 0.695 | 100 | 20 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
25 | 2.5x2.5x2 | 0.72 | 120 | 25 | 3.49 | 56451.6129 | 2100 | 93% | 52500 | 16.1752 | 71.89 | 0.44931 | 2 | 25 | 2.5x2.5x2 | 0.72 | 120 | 25 | 3.3 | 56451.6129 | 2100 | 93% | 52500 | 17.1065 | 52.48 | 0.47518 | 1.46 | 25 | 2.5x2.5x2 | 0.72 | 120 | 25 | 4.68 | 56451.6129 | 2100 | 93% | 52500 | 12.0623 | 18.09 | 0.33506 | 0.51 | 25 | 2.5x2.5x2 | 0.72 | 120 | 25 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
30 | 2.5x2.5x2 | 0.945 | 150 | 30 | 3.49 | 67741.9355 | 2100 | 93% | 63000 | 19.4103 | 86.27 | 0.53917 | 2.4 | 30 | 2.5x2.5x2 | 0.945 | 150 | 30 | 3.3 | 67741.9355 | 2100 | 93% | 63000 | 20.5279 | 62.97 | 0.57022 | 1.75 | 30 | 2.5x2.5x2 | 0.945 | 150 | 30 | 4.68 | 67741.9355 | 2100 | 93% | 63000 | 14.4748 | 21.71 | 0.40208 | 0.61 | 30 | 2.5x2.5x2 | 0.945 | 150 | 30 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
35 | 2.5x2.5x2 | 0.978 | 190 | 35 | 3.49 | 79032.2581 | 2100 | 93% | 73500 | 22.6453 | 100.65 | 0.62904 | 2.8 | 35 | 2.5x2.5x2 | 0.978 | 190 | 35 | 3.3 | 79032.2581 | 2100 | 93% | 73500 | 23.9492 | 73.47 | 0.66525 | 2.05 | 35 | 2.5x2.5x2 | 0.978 | 190 | 35 | 4.68 | 79032.2581 | 2100 | 93% | 73500 | 16.8872 | 25.32 | 0.46909 | 0.71 | 35 | 2.5x2.5x2 | 0.978 | 190 | 35 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
40 | 2.5x2.5x2 | 1 | 230 | 40 | 3.49 | 90322.5806 | 2100 | 93% | 84000 | 25.8804 | 115.03 | 0.7189 | 3.2 | 40 | 2.5x2.5x2 | 1 | 230 | 40 | 3.3 | 90322.5806 | 2100 | 93% | 84000 | 27.3705 | 83.96 | 0.76029 | 2.34 | 40 | 2.5x2.5x2 | 1 | 230 | 40 | 4.68 | 90322.5806 | 2100 | 93% | 84000 | 19.2997 | 28.94 | 0.5361 | 0.81 | 40 | 2.5x2.5x2 | 1 | 230 | 40 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
45 | 2.5x2.5x2 | 1.06 | 270 | 45 | 3.49 | 101612.9032 | 2100 | 93% | 94500 | 29.1154 | 129.41 | 0.80876 | 3.6 | 45 | 2.5x2.5x2 | 1.06 | 270 | 45 | 3.3 | 101612.9032 | 2100 | 93% | 94500 | 30.7918 | 94.46 | 0.85533 | 2.63 | 45 | 2.5x2.5x2 | 1.06 | 270 | 45 | 4.68 | 101612.9032 | 2100 | 93% | 94500 | 21.7122 | 32.56 | 0.60312 | 0.91 | 45 | 2.5x2.5x2 | 1.06 | 270 | 45 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
49 | 2.5x2.5x2 | 1.3 | 310 | 50 | 3.49 | 112903.2258 | 2100 | 93% | 105000 | 32.3505 | 143.78 | 0.89862 | 4 | 49 | 2.5x2.5x2 | 1.3 | 310 | 50 | 3.3 | 112903.2258 | 2100 | 93% | 105000 | 34.2131 | 104.95 | 0.95036 | 2.92 | 49 | 2.5x2.5x2 | 1.3 | 310 | 49 | 4.68 | 110645.1613 | 2100 | 93% | 102900 | 23.6421 | 35.45 | 0.65673 | 0.99 | 49 | 2.5x2.5x2 | 1.3 | 310 | 49 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
60 | 2.5x2.5x2 | 1.33 | 340 | 60 | 3.49 | 135483.871 | 2100 | 93% | 126000 | 38.8206 | 172.54 | 1.0783 | 4.8 | 60 | 2.5x2.5x2 | 1.33 | 340 | 60 | 3.3 | 135483.871 | 2100 | 93% | 126000 | 41.0557 | 125.94 | 1.1404 | 3.5 | 60 | 2.5x2.5x2 | 1.33 | 340 | 60 | 4.68 | 135483.871 | 2100 | 93% | 126000 | 28.9495 | 43.41 | 0.80415 | 1.21 | 60 | 2.5x2.5x2 | 1.33 | 340 | 60 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
70 | 2.5x2.5x2 | 1.35 | 370 | 70 | 3.49 | 158064.5161 | 2100 | 93% | 147000 | 45.2907 | 201.3 | 1.2581 | 5.6 | 70 | 2.5x2.5x2 | 1.35 | 370 | 70 | 3.3 | 158064.5161 | 2100 | 93% | 147000 | 47.8983 | 146.93 | 1.3305 | 4.09 | 70 | 2.5x2.5x2 | 1.35 | 370 | 70 | 4.68 | 158064.5161 | 2100 | 93% | 147000 | 33.7745 | 50.64 | 0.93818 | 1.41 | 70 | 2.5x2.5x2 | 1.35 | 370 | 70 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
75 | 2.5x2.5x2 | 1.54 | 400 | 75 | 3.49 | 169354.8387 | 2100 | 93% | 157500 | 48.5257 | 215.67 | 1.3479 | 6 | 75 | 2.5x2.5x2 | 1.54 | 400 | 75 | 3.3 | 169354.8387 | 2100 | 93% | 157500 | 51.3196 | 157.43 | 1.4255 | 4.38 | 75 | 2.5x2.5x2 | 1.54 | 400 | 75 | 4.68 | 169354.8387 | 2100 | 93% | 157500 | 36.1869 | 54.26 | 1.0052 | 1.51 | 75 | 2.5x2.5x2 | 1.54 | 400 | 75 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
85 | 2.5x2.5x2 | 1.56 | 480 | 85 | 3.49 | 191935.4839 | 2100 | 93% | 178500 | 54.9958 | 244.43 | 1.5277 | 6.79 | 85 | 2.5x2.5x2 | 1.56 | 480 | 85 | 3.3 | 191935.4839 | 2100 | 93% | 178500 | 58.1623 | 178.42 | 1.6156 | 4.96 | 85 | 2.5x2.5x2 | 1.56 | 480 | 85 | 4.68 | 191935.4839 | 2100 | 93% | 178500 | 41.0119 | 61.49 | 1.1392 | 1.71 | 85 | 2.5x2.5x2 | 1.56 | 480 | 85 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
100 | 2.5x2.5x2 | 2.38 | 620 | 100 | 3.49 | 225806.4516 | 2100 | 93% | 210000 | 64.701 | 287.56 | 1.7972 | 7.99 | 100 | 2.5x2.5x2 | 2.38 | 620 | 100 | 3.3 | 225806.4516 | 2100 | 93% | 210000 | 68.4262 | 209.9 | 1.9007 | 5.84 | 100 | 2.5x2.5x2 | 2.38 | 620 | 100 | 4.68 | 225806.4516 | 2100 | 93% | 210000 | 48.2492 | 72.34 | 1.3403 | 2.01 | 100 | 2.5x2.5x2 | 2.38 | 620 | 100 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
120 | 2.5x2.5x2 | 2.42 | 700 | 120 | 3.49 | 270967.7419 | 2100 | 93% | 252000 | 77.6412 | 345.08 | 2.1567 | 9.59 | 120 | 2.5x2.5x2 | 2.42 | 700 | 120 | 3.3 | 270967.7419 | 2100 | 93% | 252000 | 82.1114 | 251.88 | 2.2809 | 7 | 120 | 2.5x2.5x2 | 2.42 | 700 | 120 | 4.68 | 270967.7419 | 2100 | 93% | 252000 | 57.8991 | 86.81 | 1.6083 | 2.42 | 120 | 2.5x2.5x2 | 2.42 | 700 | 120 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
145 | 2.5x2.5x2 | 2.46 | 780 | 145 | 3.49 | 327419.3548 | 2100 | 93% | 304500 | 93.8164 | 416.97 | 2.606 | 11.59 | 145 | 2.5x2.5x2 | 2.46 | 780 | 145 | 3.3 | 327419.3548 | 2100 | 93% | 304500 | 99.218 | 304.35 | 2.7561 | 8.46 | 145 | 2.5x2.5x2 | 2.46 | 780 | 145 | 4.68 | 327419.3548 | 2100 | 93% | 304500 | 69.9614 | 104.89 | 1.9434 | 2.92 | 145 | 2.5x2.5x2 | 2.46 | 780 | 145 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
160 | 2.5x3x2 | 3.1 | 750 | 160 | 3.49 | 361290.3226 | 2100 | 93% | 336000 | 103.5216 | 460.1 | 2.8756 | 12.79 | 150 | 2.5x3x2 | 3.1 | 750 | 160 | 3.3 | 361290.3226 | 2100 | 93% | 336000 | 109.4819 | 335.84 | 3.0412 | 9.33 | 150 | 2.5x3x2 | 3.1 | 750 | 160 | 4.68 | 361290.3226 | 2100 | 93% | 336000 | 77.1988 | 115.75 | 2.1444 | 3.22 | 150 | 2.5x3x2 | 3.1 | 750 | 160 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
240 | 4.5x4.5x3.2 | 3.2 | 750 | 240 | 3.49 | 541935.4839 | 2100 | 93% | 504000 | 155.2824 | 690.15 | 4.3134 | 19.18 | 240 | 4.5x4.5x3.2 | 3.2 | 750 | 240 | 3.3 | 541935.4839 | 2100 | 93% | 504000 | 164.2229 | 503.76 | 4.5617 | 14 | 240 | 4.5x4.5x3.2 | 3.2 | 750 | 240 | 4.68 | 541935.4839 | 2100 | 93% | 504000 | 115.7982 | 173.62 | 3.2166 | 4.83 | 240 | 4.5x4.5x3.2 | 3.2 | 750 | 240 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
300 | 4.5x4.5x3.2 | 4 | 1000 | 300 | 3.49 | 677419.3548 | 2100 | 93% | 630000 | 194.103 | 862.68 | 5.3917 | 23.97 | 300 | 4.5x4.5x3.2 | 4 | 1000 | 300 | 3.3 | 677419.3548 | 2100 | 93% | 630000 | 205.2786 | 629.69 | 5.7022 | 17.5 | 300 | 4.5x4.5x3.2 | 4 | 1000 | 300 | 4.68 | 677419.3548 | 2100 | 93% | 630000 | 144.7477 | 217.02 | 4.0208 | 6.03 | 300 | 4.5x4.5x3.2 | 4 | 1000 | 300 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
360 | 4.5x4.5x3.2 | 4 | 1000 | 360 | 3.49 | 812903.2258 | 2100 | 93% | 756000 | 232.9236 | 1035.22 | 6.4701 | 28.76 | 360 | 4.5x4.5x3.2 | 4 | 1000 | 360 | 3.3 | 812903.2258 | 2100 | 93% | 756000 | 246.3343 | 755.63 | 6.8426 | 20.99 | 360 | 4.5x4.5x3.2 | 4 | 1000 | 360 | 4.68 | 812903.2258 | 2100 | 93% | 756000 | 173.6973 | 260.42 | 4.8249 | 7.24 | 360 | 4.5x4.5x3.2 | 4 | 1000 | 360 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
450 | 6x6x4 | 6 | 1400 | 450 | 3.49 | 1016129.0323 | 2100 | 93% | 945000 | 291.1545 | 1294.02 | 8.0876 | 35.95 | 450 | 6x6x4 | 6 | 1400 | 450 | 3.3 | 1016129.0323 | 2100 | 93% | 945000 | 307.9179 | 944.54 | 8.5533 | 26.24 | 450 | 6x6x4 | 6 | 1400 | 450 | 4.68 | 1016129.0323 | 2100 | 93% | 945000 | 217.1216 | 325.52 | 6.0312 | 9.05 | 450 | 6x6x4 | 6 | 1400 | 450 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
550 | 6x6x4 | 6 | 1400 | 550 | 3.49 | 1241935.4839 | 2100 | 93% | 1155000 | 355.8554 | 1581.58 | 9.8849 | 43.94 | 550 | 6x6x4 | 6 | 1400 | 550 | 3.3 | 1241935.4839 | 2100 | 93% | 1155000 | 376.3441 | 1154.43 | 10.454 | 32.07 | 550 | 6x6x4 | 6 | 1400 | 550 | 4.68 | 1241935.4839 | 2100 | 93% | 1155000 | 265.3708 | 397.86 | 7.3714 | 11.06 | 550 | 6x6x4 | 6 | 1400 | 550 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
700 | 6x6x4 | 9 | 2300 | 700 | 3.49 | 1580645.1613 | 2100 | 93% | 1470000 | 452.9069 | 2012.92 | 12.5807 | 55.92 | 700 | 6x6x4 | 9 | 2300 | 700 | 3.3 | 1580645.1613 | 2100 | 93% | 1470000 | 478.9834 | 1469.28 | 13.3051 | 40.82 | 700 | 6x6x4 | 9 | 2300 | 700 | 4.68 | 1580645.1613 | 2100 | 93% | 1470000 | 337.7447 | 506.37 | 9.3818 | 14.07 | 700 | 6x6x4 | 9 | 2300 | 700 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
900 | 6x6x4 | 9 | 2300 | 900 | 3.49 | 2032258.0645 | 2100 | 93% | 1890000 | 582.3089 | 2588.04 | 16.1752 | 71.89 | 900 | 6x6x4 | 9 | 2300 | 900 | 3.3 | 2032258.0645 | 2100 | 93% | 1890000 | 615.8358 | 1889.07 | 17.1065 | 52.48 | 900 | 6x6x4 | 9 | 2300 | 900 | 4.68 | 2032258.0645 | 2100 | 93% | 1890000 | 434.2432 | 651.04 | 12.0623 | 18.09 | 900 | 6x6x4 | 9 | 2300 | 900 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1200 | 6x6x4.5 | 11.8 | 3100 | 1200 | 3.49 | 2709677.4194 | 2100 | 93% | 2520000 | 776.4119 | 3450.72 | 21.567 | 95.86 | 1200 | 6x6x4.5 | 11.8 | 3100 | 1200 | 3.3 | 2709677.4194 | 2100 | 93% | 2520000 | 821.1144 | 2518.76 | 22.8087 | 69.97 | 1200 | 6x6x4.5 | 11.8 | 3100 | 1200 | 4.68 | 2709677.4194 | 2100 | 93% | 2520000 | 578.9909 | 868.06 | 16.0831 | 24.12 | 1200 | 6x6x4.5 | 11.8 | 3100 | 1200 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1600 | 8x7x4.5 | 14 | 3300 | 1600 | 3.49 | 3612903.2258 | 2100 | 93% | 3360000 | 1035.2158 | 4600.96 | 28.756 | 127.81 | 1600 | 8x7x4.5 | 14 | 3300 | 1600 | 3.3 | 3612903.2258 | 2100 | 93% | 3360000 | 1094.8192 | 3358.35 | 30.4116 | 93.29 | 1600 | 8x7x4.5 | 14 | 3300 | 1600 | 4.68 | 3612903.2258 | 2100 | 93% | 3360000 | 771.9879 | 1157.41 | 21.4441 | 32.16 | 1600 | 8x7x4.5 | 14 | 3300 | 1600 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2000 | 8.5x7x5 | 19 | 4700 | 2000 | 3.49 | 4516129.0323 | 2100 | 93% | 4200000 | 1294.0198 | 5751.2 | 35.945 | 159.76 | 2000 | 8.5x7x5 | 19 | 4700 | 2000 | 3.3 | 4516129.0323 | 2100 | 93% | 4200000 | 1368.5239 | 4197.93 | 38.0146 | 116.61 | 2000 | 8.5x7x5 | 19 | 4700 | 2000 | 4.68 | 4516129.0323 | 2100 | 93% | 4200000 | 964.9848 | 1446.76 | 26.8051 | 40.19 | 2000 | 8.5x7x5 | 19 | 4700 | 2000 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
3000 |  |  |  | 3000 | 3.49 | 6774193.5484 | 2100 | 93% | 6300000 | 1941.0297 | 8626.8 | 53.9175 | 239.64 | 3000 |  |  |  | 3000 | 3.3 | 6774193.5484 | 2100 | 93% | 6300000 | 2052.7859 | 6296.89 | 57.0218 | 174.92 | 3000 |  |  |  | 3000 | 4.68 | 6774193.5484 | 2100 | 93% | 6300000 | 1447.4773 | 2170.14 | 40.2077 | 60.29 | 3000 |  |  |  | 3000 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4000 |  |  |  | 4000 | 3.49 | 9032258.0645 | 2100 | 93% | 8400000 | 2588.0396 | 11502.4 | 71.89 | 319.52 | 4000 |  |  |  | 4000 | 3.3 | 9032258.0645 | 2100 | 93% | 8400000 | 2737.0479 | 8395.86 | 76.0291 | 233.22 | 4000 |  |  |  | 4000 | 4.68 | 9032258.0645 | 2100 | 93% | 8400000 | 1929.9697 | 2893.51 | 53.6103 | 80.38 | 4000 |  |  |  | 4000 | 4.361 | #DIV/0! | 0 | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Boiler size | Boiler room | Boiler weight | Water | Boiler size | kWh | P/energy/demand | Full Load | Annual boiler eff. | F/energy/demand | tonnes | M3/Yr | 1/wk/Winter | 1 wk winter | Boiler size | Boiler room | Boiler weight | Water | Boiler size | kWh | P/energy/demand | Full Load | Annual boiler eff. | F/energy/output | tonnes | M3/Yr | 1/wk/Winter | 1 wk winter | Boiler size | Boiler room | Boiler weight | Water | Boiler size | kWh | P/energy/demand | Full Load | Annual boiler eff. | F/energy/demand | tonnes | M3/Yr | 1/wk/Winter | 1 wk winter | Boiler size | Boiler room | Boiler weight | Water | Boiler size | kWh | P/energy/demand | Full Load | Annual boiler eff. | F/energy/demand | tonnes | M3/Yr | 1/wk/Winter | 1 wk winter
kW | LxWxH | Tonnes | Litres | kW | kg |  | Operating Hrs | % |  | year | m3 | Tonnes | m3 | kW | LxWxH | Tonnes | Litres | kW | kg |  | Operating Hrs | % | FLOH - Med | year | M3 | Tonnes | M3 | kW | LxWxH | Tonnes | Litres | kW | kg |  | Operating Hrs | % |  | year | m3 | Tonnes | m3 | kW | LxWxH | Tonnes | Litres | kW | kg |  | Operating Hrs | % |  | year | m3 | Tonnes | m3
APPROX. BOILER SPECIFICATIONS |  |  |  | CW WOODCHIP | [9 empty] | APPROX. BOILER SPECIFICATIONS |  |  |  | NCH WOODCHIP | [9 empty] | APPROX. BOILER SPECIFICATIONS |  |  |  | Wood Pellets | [9 empty] | APPROX. BOILER SPECIFICATIONS |  |  |  | Miscanthus Pellets
|  |  |  | FLEH - School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%) | [13 empty] | FLEH - School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%) | [13 empty] | FLEH - School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%) | [13 empty] | FLEH - School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Chip P30 M30 - Energy Use - kWh - Delivery - Storage
CW chips P30 M30
% M |  | Delivery/tonnes |  | Delivery |  | kWh
|  | 1wk/winter/use/t |  | m3 |  | load
30 |  | 38.65 |  | 171.78 |  | 134888.5
CW Chip - Storage
Full store |  | Full store/woodchip |  | Full store |  | Full store
m3 |  | tonnes |  | kWh |  | weeks/winter/supply
1627.5 |  | 366.1875 |  | 1277994.375 |  | 9.4745
NCH chip - Delivery
% M |  | Delivery/tonnes |  | Delivery |  | kWh
|  | 1wk/winter/use/t |  | m3 |  | load
30 |  | 40.88 |  | 125.4 |  | 134904
NCH Chip - Storage
Full store |  | Full store/woodchip |  | Full store |  | Full store
m3 |  | tonnes |  | kWh |  | weeks/winter/supply
1627.5 |  | 528.9375 |  | 1745493.75 |  | 12.9388
Pellet - Delivery
kWh/tonne |  | Delivery/tonnes |  | Delivery |  | kWh
|  | 1wk/winter/use/t |  | m3 |  | load
4700 |  | 2.01 |  | 2.97 |  | 9447
Pellet - Storage
Full store |  | Full store/pellets |  | Full store |  | Full Load
m3 |  | tonnes |  | kWh |  | weeks/supply
40 |  | 26.68 |  | 125396 |  | 13.2736
Pellet - Delivery
kWh/tonne |  | Delivery/tonnes |  | Delivery |  | kWh
|  | 1wk/winter/use/t |  | m3 |  | load
4361 |  | 0 |  | 0 |  | 0
Pellet - Storage
Full store |  | Full store/pellets |  | Full store |  | Full Load
m3 |  | tonnes |  | kWh |  | weeks/supply
0 |  | 0 |  | 0 |  | #DIV/0!
Very Low Cost
£ CW Chip Store |  | 1627.5 | 488250
£ NCH Chip Store |  | 1627.5 | 488250
£ Pellet Store |  | 40 | 12000
Low Cost - SPONDS 08
£ CW Chip Store |  | 1627.5 | 699825
£ NCH Chip Store |  | 1627.5 | 699825
£ Pellet Store |  | 40 | 17200
Med Cost - SPONDS 08
£ SoftwoodChip Store |  | 1627.5 | 943950
£ HardwoodChip Store |  | 1627.5 | 943950
£ Pellet Store |  | 40 | 23200
High Cost - SPONDS 08
£ CW Chip Store |  | 1627.5 | 1188075
£ NCH Chip Store |  | 1627.5 | 1188075
£ Pellet Store |  | 40 | 29200
Woodchip store - Building cost calculator
m3 Woodchip store
Only alter yellow boxes
Width/m | Length/m | Height/m | m3
0 | 0 | 0 | 0
Agricultual building costs excl. VAT (SPONDS)
m3 | 100
Very Low cost price |  |  |  | Not SPONDS
m2 | Cost/m3 | £/Cost of fuel store
100 | 300 | 30000
Low cost |  |  |  | Agric. Building costs excl. VAT (SPONDS)
m2 | Cost/m3 | £/Cost of fuel store
100 | 430 | 43000
Med cost
m2 | Cost/m3 | £/Cost of fuel store
100 | 580 | 58000
High cost
m2 | Cost/m3 | £/Cost of fuel store
100 | 730 | 73000

## Conversion Tables
Conversion Tables
Watts / m2 | 0 | FLEH | 0 |  | kWh /m2 | 0 | FLEH | 0
|  | kWh / m2 | 0 |  |  |  | Watts / m2 | #DIV/0!
Heating weeks per year |  | 8760 | FLEH |  | W/hr | 0 | MWh | 0
Heating weeks per year |  | 0 | 0 |  |  |  | kWh | 0
Heating days per week |  | 0 | Load Factor % |  |  |  | MJ | 0
Heating hours per heating day |  | 0 | 0% |  |  |  | BTU | 0
FLEH | 1400 | Annual Hours % | 15.98% |  | Annual Hours % | 15.98% | FLEH | 1399.848
kW | 0 | Power |  |  | kWh | 0 | Energy
FLEH | 0 | Ave. 2190 | FLEH = Full Load Equivalent Hours |  | FLEH | 0 | Ave. 2190 | FLEH = Full Load Equivalent Hours
kWh | 0 | Energy | Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%) |  | kW | #DIV/0! | Power | Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
kWh/kg | 0 | MJ | 0 |  | MJ | 0 | kWh/kg | 0
kWh | 0 | GWh | 0 |  | BTU | 0 | GWh | 0
|  | MWh | 0 |  |  |  | MWh | 0
|  | BTU | 0 |  |  |  | kWh | 0
|  | GJ | 0 |  |  |  | GJ | 0
|  | MJ | 0 |  |  |  | MJ | 0
|  | W | 0 |  |  |  | W | 0
MJ | 0 | MWh | 0 |  | GJ | 0 | MWh | 0
|  | kWh | 0 |  |  |  | kWh | 0
|  | GJ | 0 |  |  |  | MJ | 0
|  | BTU | 0 |  |  |  | BTU | 0
|  | W | 0 |  |  |  | W | 0
MWh | 0 | kWh | 0 |  | GWh | 0 | kWh | 0
|  | GWh | 0 |  |  |  | MWh | 0
|  | BTU | 0 |  |  |  | BTU | 0
|  | GJ | 0 |  |  |  | GJ | 0
ft | 0 | m | 0 |  | m | 0 | ft | 0
ft2 | 0 | m2 | 0 |  | m2 | 0 | ft2 | 0
Hoppus ft | 0 | m3 | 0 |  | m3 | 0 | Hoppus ft | 0
Acres | 0 | Ha | 0 |  | Ha | 0 | Acres | 0
°F | 0 | °C | -17.7778 |  |  |  | Heating Oil / L | 0
[7 empty] | kWh | 0
°C | 0 | °F | 32
Average room temp 21°C - 70°F | [6 empty] | kWh | 0
From | 0 | to | 0 | #DIV/0! |  |  | Heating Oil / L | 0
What is | 0 | of | 0 | #DIV/0! |  |  | Heating Oil / L | 0
[7 empty] | BTU | 0
Fraction | 0 | % | 0%
[7 empty] | BTU | 0
% | 0% | Fraction | 0 |  |  |  | Heating Oil / L | 0
Total | 0 | % | 0% | Saving | 0 | Sum | 0
Sum | 0 | % | 0% | Total | #DIV/0! | Saving | #DIV/0!
|  | % of Total | 31.96%
Total | 8760 |  |  | Cost | 2800 | Saving | 5960
|  | % Saving of Total | 68.04%

## 1 Yr Oil Use Feasibility Study
© Biomass Wizard
| Property/Project | [7 empty] | Fuel | Litres | Primary kWh | Boiler eff. | Final kWh
[9 empty] | Oil | 0 | 0 | 0% | 0
| Heating Oil Use / Litres |  | 30000 |  | Old Boiler Efficiency |  | 80% |  |  | 0 | 0 |  | 0
[5 empty] | Primary / kWh |  | 325500 |  | Oil / Litres / Year | 0 |  | £ Oil / Year | 0
[5 empty] | Output / kWh |  | 260400 |  | Cost of oil / Litre | 0 |  | Litres / Oil / Yr | 0
| Date | [7 empty] | £ / Oil / Year | 0 |  | £ Oil / Litre | 0
| Job number | [7 empty] | kWh / Year | 0 |  | kWh / Year | 0
Project partners
[9 empty] | £ Oil / Year |  | 0
[9 empty] | Oil / litres / Year |  | 0
[9 empty] | Ave. Cost of Oil / Litre |  | 0
[9 empty] | Heating Oil / Litres |  | 0
[9 empty] | kWh |  | 0
[9 empty] | kWh |  | 0
[9 empty] | Heating Oil / Litres |  | 0
[9 empty] | Heating weeks per year |  | 8760 |  | Full Load Equivalent Hours
[9 empty] | Heating weeks per year |  | 0 |  | 0
[9 empty] | Heating days per week |  | 0 |  | Load Factor %
[9 empty] | Heating hours per heating day |  | 0 |  | 0%
School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
[9 empty] | Primary kWh |  | 0
[9 empty] | Final Heating Output |  | 0
[9 empty] | Full Load Equivalent Hours |  | 0
[9 empty] | Boiler Efficiency |  | 0%
[9 empty] | Boiler Size |  | 0
New Biomass Heating & Hot Water
Heating (kW) |  | 124
Full Load Equivalent Hours |  | 2100 |  | School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Primary Heating kWh |  | 280000
Boiler Efficiency |  | 93% |  | Ave. = 85% - DH = 75%
Final Heating output kWh |  | 260400
Extra Heating & Hot Water
Primary Hot Water kWh |  | 0
Output Hot Water/kWh |  | 0 |  | Ave 4 bedroom house = 3,742 School = 12,000 - 25,000
Hot water kW |  | 0
Total boiler size |  | 124
Boiler size |  | 150
to be installed
Total Boiler Size Required |  | 124 | kW Installed |  | 150 | % required boiler size |  | 121%
Biomass Heating & Hot Water
Heating |  | 280000
Primary kWh
Heating |  | 260400
Output kWh
Hot Water |  | 0
Primary kWh
Hot Water |  | 0
Output kWh
Total Primary |  | 280000
kWh
Total Output |  | 260400
kWh
Boiler size kW |  | 124
Buffer Vessel Sizing
Boiler size kW |  | 124
Litres/kW |  | 15 |  | Optimum size 15-20 litres per kW
Buffer Vessel/litres |  | 1860
20-100 litres/kW - Specialist assessment is required to correctly specifiy boiler and buffer vessel sizing
Fuel Requirements
[5 empty] | P30 W30 chip |  | 2.2286
tonnes/week/winter
P30 W30 chip |  | 80.2292 |  |  | P30 W30 chip |  | 9.91
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 40
P30 W30 chip |  | 356.5743 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 4.0363
Winter supply/weeks
[5 empty] | P30 W30 NCH Chip |  | 2.3569
tonnes/week/winter
P30 W30 NCH Chip |  | 84.8485 |  |  | P30 W30 chip |  | 10.48
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 40
P30 W30 NCH Chip |  | 260.2714 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 3.8168
Winter supply/weeks
[5 empty] | Pellets |  | 1.6619
tonnes/week/winter
Pellets |  | 59.8291 |  |  | Pellets |  | 2.5
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 40
Pellets |  | 89.6987 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 16
Winter supply/weeks
CO2 Comparison
Gas |  | 48.174 |  |  | Heating Oil |  | 70.28
CO2/tonnes/Year |  |  |  |  | CO2/tonnes/Year
Woodfuel |  | 6.51 |  |  | Woodfuel |  | 7
CO2/tonnes/Year |  |  |  |  | CO2/tonnes/Year
CO2 tonnes/year |  | 41.664 |  |  | CO2 tonnes/year |  | 63.28
Saving over gas |  |  |  |  | Saving over oil
Check List |  | Suitable | Unsuitable | Modification | New | Not
|  |  |  | required |  | necessary
|  | y/n | y/n | y/n | y/n | y/n
Boiler house location
Fuel store location
Piping routes
Fuel store size
Log storage
Lorry access
Electric supply
Water supply
Heating system
Building Heat Loss Assessment
BMS
Controls - Weather compensation
Controls - Optimun start/stop
Zoning
Notes
Fuel choice, boiler house & fuel store |  |  |  | Boiler house & fuel store
Check List |  | y/n |  | Check List |  | y/n
Woodchip boiler |  |  |  | New boiler house
Wood Pellet boiler |  |  |  | New fuel store
Miscanthus Pellet boiler |  |  |  | Best site location *
Log boiler |  |  |  | New Access Road
Microgeneration Certificate
Notes
Fuel delivery method/s |  |  |  | Notes
Check List |  |  | y/n
Above ground
Below ground
Walking floor
Hook-bin
Tipped delivery
* Blown delivery
Walking floor & auger
Sweep collector
Auger feed & angled floor
Sweep arm recoil switch
* Always include blown delivery
Check List |  |  | y/n | Notes
Asbestos removal
Buffer vessels
Flue
Flue fan
Ceramic flue filter
Heat meters
Solar heating
RHI
SALEX
Check List |  |  | y/n | Notes
Fuel store sizing
Sealed fuel store
Delivery pipes/sizing
Correct delivery fittings
Dust extraction
Door/spigot/slats
Ventilation
Fuel door safety cut-off
Fuel site glass
Fuel Store Contents - Ultrasonic Monitoring
Exterior lighting
Heat detector/cut off
Matched door key
Reset instructions
Photographs
Fuel supply
Chipping service
Wood & chip delivery equipment
Chip storage
Permissions & Drawings
Check List |  |  | y/n | Check List |  |  | y/n
Planning Permission |  |  |  | Civil Engineering Drawings
Building Regulations |  |  |  | Piping Drawings
CDM Regulations |  |  |  | System Drawings
Confined Space Regulations |  |  |  | Flow & Return design
EHO Permission |  |  |  | Buffer Vessel/Thermal Storage Design
EIA |  |  |  | Flue Specification / Drawings
Habitat Regulations |  |  |  | Boiler House Synoptic Map
TPO
Archaeology
Notes
Current boiler sizing
|  | Boiler Location |  | kW | Boiler Location |  | kW
0
Oil
boiler size/s
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Oil boilers - kWh is a guide as traditionally boilers were over specified
|  | Boiler Location |  | kW | Boiler Location |  | kW
Gas
boiler size/s
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Gas boilers - kWh is a guide as traditionally boilers were over specified
Electric |  | kWh
kWh |  | 0
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Biomass Boiler |  | 0 |  | kWh |  | 0
Size kW
Boiler sizing based on current boiler sizes should be avoided as traditionally boilers were over specified
Boiler sizing based on current fuel usage
Fuel Usage |  | Year 1 | Old Boiler |  | Final kWh | New Boiler
|  |  | Primary kWh | Boiler eff. |  | Boiler eff. | kW boiler
Oil usage / Litres |  | 30000 | 325500 | 80% | 260400 | 93% | 124
Gas usage / kWh |  | 325500 | 325500 | 80% | 260400 | 93% | 124
Electric usage / kWh |  | 325500 | 325500 | 80% | 260400 | 93% | 124
Boiler Size |  | 372
Notes
Quotation |  | 0 |  |  | kW boiler size
to be installed
150
Final |  | 0
installation cost
A biomass report should be produced alongside this pre-install form . The report should include:
A description of the site and surrounding facilities.
Describe building uses that will have an influence on boiler sizing e.g. sports halls, special temprature needs and kitchens etc.
Describe links with other renewables and any boiler sizing. Include buffer vessel / clorifier with solar coil recommendations.
Limitations and constraints - Deliveries, location of boiler and fuel store, noise and emissions.
A report on existing systems - conditions, life expectancy, maintenance costs, likely replacement.
List existing equipment to be used or replaced.
Existing revenue usage - Detailed analysis of existing running costs, including fuel.
A proposed biomass strategy - Include other renewables such as solar water heating, reduction in load from increased thermal insulation or fabric changes, use of buffer vessels. Create a summer water heating and low-load strategy. Outline proposed biomass boiler sizing with justification in terms of heat loads and boiler sizing. Create controls and zoning.
Estimated capital costs - Produce a summary of estimated capital costs with assumptions and an overview of all components and capital costs.
Plans/site layout - Show proposed location of boiler/s and fuel storage, layout of heating mains and district heating layout with accurate measurements. Layout of deliveries, access, reversing and parking.
Links with other projects - Review any projects likely to happen within the short-term (1-2 yrs), medium (2-5 yrs) and long-term (5yrs+) along with implications and risks.
Maintenance - Produce a summary of maintenance, implications and likely costs.
Benefits - Detail benefits and reasons for undertaking this scheme i.e.. carbon, CO2, local employment.
DECC rating - Produce an estimated DECC rating with biomass to prove how biomass will improve the DECC rating.
Financial analysis - Detailed financial analysis that includes total capital cost, capital cost per kW and cost per tonne of carbon saved.
Risk assessment - Detail all risks.
Summary - A detailed overview with concise recommendations.

## 2 Yr Oil Use Feasibility Study
© Biomass Wizard
| Property/Project | [7 empty] | Fuel | Litres | Primary kWh | Boiler eff. | Final kWh
[9 empty] | Oil | 0 | 0 | 0% | 0
| Heating Oil Use / Litres |  | Year 1 | 30000 |  | Year 2 | 30000 |  |  | 0 | 0 |  | 0
| Old Boiler Efficiency |  | 80% |  |  | Ave. | 30000 |  | Oil / Litres / Year | 0 |  | £ Oil / Year | 0
[9 empty] | Cost of oil / Litre | 0 |  | Litres / Oil / Yr | 0
| Date |  |  |  | Primary / kWh |  | 325500 |  | £ / Oil / Year | 0 |  | £ Oil / Litre | 0
| Job number |  |  |  | Output kWh |  | 260400 |  | kWh / Year | 0 |  | kWh / Year | 0
Project partners
[9 empty] | £ Oil / Year |  | 0
[9 empty] | Oil / litres / Year |  | 0
[9 empty] | Ave. Cost of Oil / Litre |  | 0
[9 empty] | Heating Oil / Litres |  | 0
[9 empty] | kWh |  | 0
[9 empty] | kWh |  | 0
[9 empty] | Heating Oil / Litres |  | 0
[9 empty] | Heating weeks per year |  | 8760 |  | Full Load Equivalent Hours
[9 empty] | Heating weeks per year |  | 0 |  | 0
[9 empty] | Heating days per week |  | 0 |  | Load Factor %
[9 empty] | Heating hours per heating day |  | 0 |  | 0%
School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
[9 empty] | Primary kWh |  | 0
[9 empty] | Final Heating Output |  | 0
[9 empty] | Full Load Equivalent Hours |  | 0
[9 empty] | Boiler Efficiency |  | 0%
[9 empty] | Boiler Size |  | 0
Biomass Heating & Hot Water
Heating (kW) |  | 124
Full Load Equivalent Hours |  | 2100 |  | School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Primary Heating kWh |  | 280000
Boiler Efficiency |  | 93% |  | Ave. = 85% - DH = 75%
Final Heating output kWh |  | 260400
Extra Heating & Hot Water
Primary Hot Water kWh |  | 0
Output Hot Water/kWh |  | 0
Hot water kW |  | 0
Total boiler size |  | 124
Boiler size |  | 150
to be installed
Total Boiler Size Required |  | 124 | kW Installed |  | 150 | % required boiler size |  | 121%
Biomass Heating & Hot Water
Heating |  | 280000
Primary kWh
Heating |  | 260400
Output kWh
Hot Water |  | 0
Primary kWh
Hot Water |  | 0
Output kWh
Total Primary |  | 280000
kWh
Total Output |  | 260400
kWh
Boiler size kW |  | 124
Buffer Vessel Sizing
Boiler size kW |  | 124
Litres/kW |  | 15 |  | Optimum size 15-20 litres per kW
Buffer Vessel/litres |  | 1860
20-100 litres/kW - Specialist assessment is required to correctly specifiy boiler and buffer vessel sizing
Fuel Requirements
[5 empty] | P30 W30 chip |  | 0
tonnes/week/winter
P30 W30 chip |  | 80.2292 |  |  | P30 W30 chip |  | 0
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 0
P30 W30 chip |  | 356.5743 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 0
Winter supply/weeks
[5 empty] | P30 W30 NCH Chip |  | 0
tonnes/week/winter
P30 W30 NCH Chip |  | 84.8485 |  |  | P30 W30 chip |  | 0
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 32
P30 W30 NCH Chip |  | 260.2714 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 0
Winter supply/weeks
[5 empty] | Pellets |  | 0
tonnes/week/winter
Pellets |  | 59.8291 |  |  | Pellets |  | 0
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 0
Pellets |  | 89.6987 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 0
Winter supply/weeks
CO2 Comparison
Gas |  | 48.174 |  |  | Heating Oil |  | 70.28
CO2/tonnes/Year |  |  |  |  | CO2/tonnes/Year
Woodfuel |  | 6.51 |  |  | Woodfuel |  | 7
CO2/tonnes/Year |  |  |  |  | CO2/tonnes/Year
CO2 tonnes/year |  | 41.664 |  |  | CO2 tonnes/year |  | 63.28
Saving over gas |  |  |  |  | Saving over oil
Check List |  | Suitable | Unsuitable | Modification | New | Not
|  |  |  | required |  | necessary
|  | y/n | y/n | y/n | y/n | y/n
Boiler house location
Fuel store location
Piping routes
Fuel store size
Log storage
Lorry access
Electric supply
Water supply
Heating system
Building Heat Loss Assessment
BMS
Controls - Weather compensation
Controls - Optimun start/stop
Zoning
Notes
Fuel choice, boiler house & fuel store |  |  |  | Boiler house & fuel store
Check List |  | y/n |  | Check List |  | y/n
Woodchip boiler |  |  |  | New boiler house
Wood Pellet boiler |  |  |  | New fuel store
Miscanthus Pellet boiler |  |  |  | Best site location *
Log boiler |  |  |  | New Access Road
Microgeneration Certificate
Notes
Fuel delivery method/s |  |  |  | Notes
Check List |  |  | y/n
Above ground
Below ground
Walking floor
Hook-bin
Tipped delivery
* Blown delivery
Walking floor & auger
Sweep collector
Auger feed & angled floor
Sweep arm recoil switch
* Always include blown delivery
Check List |  |  | y/n | Notes
Asbestos removal
Buffer vessels
Flue
Flue fan
Ceramic flue filter
Heat meters
Solar heating
RHI
SALEX
Check List |  |  | y/n | Notes
Fuel store sizing
Sealed fuel store
Delivery pipes/sizing
Correct delivery fittings
Dust extraction
Door/spigot/slats
Ventilation
Fuel door safety cut-off
Fuel site glass
Fuel Store Contents - Ultrasonic Monitoring
Exterior lighting
Heat detector/cut off
Matched door key
Reset instructions
Photographs
Fuel supply
Chipping service
Wood & chip delivery equipment
Chip storage
Permissions & Drawings
Check List |  |  | y/n | Check List |  |  | y/n
Planning Permission |  |  |  | Civil Engineering Drawings
Building Regulations |  |  |  | Piping Drawings
CDM Regulations |  |  |  | System Drawings
Confined Space Regulations |  |  |  | Flow & Return design
EHO Permission |  |  |  | Buffer Vessel/Thermal Storage Design
EIA |  |  |  | Flue Specification / Drawings
Habitat Regulations |  |  |  | Boiler House Synoptic Map
TPO
Archaeology
Notes
Current boiler sizing
|  | Boiler Location |  | kW | Boiler Location |  | kW
0
Oil
boiler size/s
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Oil boilers - kWh is a guide as traditionally boilers were over specified
|  | Boiler Location |  | kW | Boiler Location |  | kW
Gas
boiler size/s
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Gas boilers - kWh is a guide as traditionally boilers were over specified
Electric |  | kWh
kWh |  | 0
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Biomass Boiler |  | 0 |  | kWh |  | 0
Size kW
Boiler sizing based on current boiler sizes should be avoided as traditionally boilers were over specified
Boiler sizing based on current fuel usage
Fuel Usage |  | Year 1 | Year 2 |  | Ave.
Oil usage / Litres |  | 30000 | 30000 |  | 30000
Gas usage / kWh |  | 325500 | 325500 |  | 325500
Electric usage / kWh |  | 325500 | 325500 |  | 325500
Fuel Usage |  | Ave. | Old Boiler |  | Final kWh | New Boiler
|  |  | Primary kWh | Boiler eff. |  | Boiler eff. | kW boiler
Oil usage / Litres |  | 30000 | 325500 | 80% | 260400 | 93% | 124
Gas usage / kWh |  | 325500 | 325500 | 80% | 260400 | 93% | 124
Electric usage / kWh |  | 325500 | 325500 | 80% | 260400 | 93% | 124
Boiler Size |  | 372
Notes
Quotation |  | 0 |  |  | kW boiler size
to be installed
150
Final |  | 0
installation cost
A biomass report should be produced alongside this pre-install form . The report should include:
A description of the site and surrounding facilities.
Describe building uses that will have an influence on boiler sizing e.g. sports halls, special temprature needs and kitchens etc.
Describe links with other renewables and any boiler sizing. Include buffer vessel / clorifier with solar coil recommendations.
Limitations and constraints - Deliveries, location of boiler and fuel store, noise and emissions.
A report on existing systems - conditions, life expectancy, maintenance costs, likely replacement.
List existing equipment to be used or replaced.
Existing revenue usage - Detailed analysis of existing running costs, including fuel.
A proposed biomass strategy - Include other renewables such as solar water heating, reduction in load from increased thermal insulation or fabric changes, use of buffer vessels. Create a summer water heating and low-load strategy. Outline proposed biomass boiler sizing with justification in terms of heat loads and boiler sizing. Create controls and zoning.
Estimated capital costs - Produce a summary of estimated capital costs with assumptions and an overview of all components and capital costs.
Plans/site layout - Show proposed location of boiler/s and fuel storage, layout of heating mains and district heating layout with accurate measurements. Layout of deliveries, access, reversing and parking.
Links with other projects - Review any projects likely to happen within the short-term (1-2 yrs), medium (2-5 yrs) and long-term (5yrs+) along with implications and risks.
Maintenance - Produce a summary of maintenance, implications and likely costs.
Benefits - Detail benefits and reasons for undertaking this scheme i.e.. carbon, CO2, local employment.
DECC rating - Produce an estimated DECC rating with biomass to prove how biomass will improve the DECC rating.
Financial analysis - Detailed financial analysis that includes total capital cost, capital cost per kW and cost per tonne of carbon saved.
Risk assessment - Detail all risks.
Summary - A detailed overview with concise recommendations.

## 3 Yr Oil Use Feasibility Study
© Biomass Wizard
| Property/Project |  |  |  |  | Year 1 | 30000 |  | Fuel | Litres | Primary kWh | Boiler eff. | Final kWh
[9 empty] | Oil | 0 | 0 | 0% | 0
| Old Boiler Efficiency |  | 80% |  |  | Year 2 | 30000 |  |  | 0 | 0 |  | 0
| Primary / kWh |  | 325500 |  |  | Year 3 | 30000 |  | Oil / Litres / Year | 0 |  | £ Oil / Year | 0
| Output kWh |  | 260400 | [5 empty] | Cost of oil / Litre | 0 |  | Litres / Oil / Yr | 0
| Date |  |  |  |  | Ave. | 30000 |  | £ / Oil / Year | 0 |  | £ Oil / Litre | 0
| Job number | [7 empty] | kWh / Year | 0 |  | kWh / Year | 0
Project partners
[9 empty] | £ Oil / Year |  | 0
[9 empty] | Oil / litres / Year |  | 0
[9 empty] | Ave. Cost of Oil / Litre |  | 0
[9 empty] | Heating Oil / Litres |  | 0
[9 empty] | kWh |  | 0
[9 empty] | kWh |  | 0
[9 empty] | Heating Oil / Litres |  | 0
[9 empty] | Heating weeks per year |  | 8760 |  | Full Load Equivalent Hours
[9 empty] | Heating weeks per year |  | 0 |  | 0
[9 empty] | Heating days per week |  | 0 |  | Load Factor %
[9 empty] | Heating hours per heating day |  | 0 |  | 0%
School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
[9 empty] | Primary kWh |  | 0
[9 empty] | Final Heating Output |  | 0
[9 empty] | Full Load Equivalent Hours |  | 0
[9 empty] | Boiler Efficiency |  | 0%
[9 empty] | Boiler Size |  | 0
Biomass Heating & Hot Water
Heating (kW) |  | 124
Full Load Equivalent Hours |  | 2100 |  | School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Primary Heating kWh |  | 280000
Boiler Efficiency |  | 93% |  | Ave. = 85% - DH = 75%
Final Heating output kWh |  | 260400
Extra Heating & Hot Water
Primary Hot Water kWh |  | 0
Output Hot Water/kWh |  | 0
Hot water kW |  | 0
Total boiler size |  | 124
Boiler size |  | 150
to be installed
Total Boiler Size Required |  | 124 | kW Installed |  | 150 | % required boiler size |  | 121%
Biomass Heating & Hot Water
Heating |  | 280000
Primary kWh
Heating |  | 260400
Output kWh
Hot Water |  | 0
Primary kWh
Hot Water |  | 0
Output kWh
Total Primary |  | 280000
kWh
Total Output |  | 260400
kWh
Boiler size kW |  | 124
Buffer Vessel Sizing
Boiler size kW |  | 124
Litres/kW |  | 15 |  | Optimum size 15-20 litres per kW
Buffer Vessel/litres |  | 1860
20-100 litres/kW - Specialist assessment is required to correctly specifiy boiler and buffer vessel sizing
Fuel Requirements
[5 empty] | P30 W30 chip |  | 2.2286
tonnes/week/winter
P30 W30 chip |  | 80.2292 |  |  | P30 W30 chip |  | 9.91
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 40
P30 W30 chip |  | 356.5743 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 4.0363
Winter supply/weeks
[5 empty] | P30 W30 NCH Chip |  | 2.3569
tonnes/week/winter
P30 W30 NCH Chip |  | 84.8485 |  |  | P30 W30 chip |  | 10.48
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 40
P30 W30 NCH Chip |  | 260.2714 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 3.8168
Winter supply/weeks
[5 empty] | Pellets |  | 1.6619
tonnes/week/winter
Pellets |  | 59.8291 |  |  | Pellets |  | 2.5
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 40
Pellets |  | 89.6987 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 16
Winter supply/weeks
CO2 Comparison
Gas |  | 48.174 |  |  | Heating Oil |  | 70.28
CO2/tonnes/Year |  |  |  |  | CO2/tonnes/Year
Woodfuel |  | 6.51 |  |  | Woodfuel |  | 7
CO2/tonnes/Year |  |  |  |  | CO2/tonnes/Year
CO2 tonnes/year |  | 41.664 |  |  | CO2 tonnes/year |  | 63.28
Saving over gas |  |  |  |  | Saving over oil
Check List |  | Suitable | Unsuitable | Modification | New | Not
|  |  |  | required |  | necessary
|  | y/n | y/n | y/n | y/n | y/n
Boiler house location
Fuel store location
Piping routes
Fuel store size
Log storage
Lorry access
Electric supply
Water supply
Heating system
Building Heat Loss Assessment
BMS
Controls - Weather compensation
Controls - Optimun start/stop
Zoning
Notes
Fuel choice, boiler house & fuel store |  |  |  | Boiler house & fuel store
Check List |  | y/n |  | Check List |  | y/n
Woodchip boiler |  |  |  | New boiler house
Wood Pellet boiler |  |  |  | New fuel store
Miscanthus Pellet boiler |  |  |  | Best site location *
Log boiler |  |  |  | New Access Road
Microgeneration Certificate
Notes
Fuel delivery method/s |  |  |  | Notes
Check List |  |  | y/n
Above ground
Below ground
Walking floor
Hook-bin
Tipped delivery
* Blown delivery
Walking floor & auger
Sweep collector
Auger feed & angled floor
Sweep arm recoil switch
* Always include blown delivery
Check List |  |  | y/n | Notes
Asbestos removal
Buffer vessels
Flue
Flue fan
Ceramic flue filter
Heat meters
Solar heating
RHI
SALEX
Check List |  |  | y/n | Notes
Fuel store sizing
Sealed fuel store
Delivery pipes/sizing
Correct delivery fittings
Dust extraction
Door/spigot/slats
Ventilation
Fuel door safety cut-off
Fuel site glass
Fuel Store Contents - Ultrasonic Monitoring
Exterior lighting
Heat detector/cut off
Matched door key
Reset instructions
Photographs
Fuel supply
Chipping service
Wood & chip delivery equipment
Chip storage
Permissions & Drawings
Check List |  |  | y/n | Check List |  |  | y/n
Planning Permission |  |  |  | Civil Engineering Drawings
Building Regulations |  |  |  | Piping Drawings
CDM Regulations |  |  |  | System Drawings
Confined Space Regulations |  |  |  | Flow & Return design
EHO Permission |  |  |  | Buffer Vessel/Thermal Storage Design
EIA |  |  |  | Flue Specification / Drawings
Habitat Regulations |  |  |  | Boiler House Synoptic Map
TPO
Archaeology
Notes
Current boiler sizing
|  | Boiler Location |  | kW | Boiler Location |  | kW
0
Oil
boiler size/s
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Oil boilers - kWh is a guide as traditionally boilers were over specified
|  | Boiler Location |  | kW | Boiler Location |  | kW
Gas
boiler size/s
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Gas boilers - kWh is a guide as traditionally boilers were over specified
Electric |  | kWh
kWh |  | 0
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Biomass Boiler |  | 0 |  | kWh |  | 0
Size kW
Boiler sizing based on current boiler sizes should be avoided as traditionally boilers were over specified
Boiler sizing based on current fuel usage
Fuel Usage |  | Year 1 | Year 2 |  | Year 1 | Ave.
Oil usage / Litres |  | 30000 | 30000 |  | 30000 | 30000
Gas usage / kWh |  | 325500 | 325500 |  | 325500 | 325500
Electric usage / kWh |  | 325500 | 325500 |  | 325500 | 325500
Fuel Usage |  | Ave. | Old Boiler |  | Final kWh | New Boiler
|  |  | Primary kWh | Boiler eff. |  | Boiler eff. | kW boiler
Oil usage / Litres |  | 30000 | 325500 | 80% | 260400 | 93% | 124
Gas usage / kWh |  | 325500 | 325500 | 80% | 260400 | 93% | 124
Electric usage / kWh |  | 325500 | 325500 | 80% | 260400 | 93% | 124
Boiler Size |  | 372
Notes
Quotation |  | 0 |  |  | kW boiler size
to be installed
150
Final |  | 0
installation cost
A biomass report should be produced alongside this pre-install form . The report should include:
A description of the site and surrounding facilities.
Describe building uses that will have an influence on boiler sizing e.g. sports halls, special temprature needs and kitchens etc.
Describe links with other renewables and any boiler sizing. Include buffer vessel / clorifier with solar coil recommendations.
Limitations and constraints - Deliveries, location of boiler and fuel store, noise and emissions.
A report on existing systems - conditions, life expectancy, maintenance costs, likely replacement.
List existing equipment to be used or replaced.
Existing revenue usage - Detailed analysis of existing running costs, including fuel.
A proposed biomass strategy - Include other renewables such as solar water heating, reduction in load from increased thermal insulation or fabric changes, use of buffer vessels. Create a summer water heating and low-load strategy. Outline proposed biomass boiler sizing with justification in terms of heat loads and boiler sizing. Create controls and zoning.
Estimated capital costs - Produce a summary of estimated capital costs with assumptions and an overview of all components and capital costs.
Plans/site layout - Show proposed location of boiler/s and fuel storage, layout of heating mains and district heating layout with accurate measurements. Layout of deliveries, access, reversing and parking.
Links with other projects - Review any projects likely to happen within the short-term (1-2 yrs), medium (2-5 yrs) and long-term (5yrs+) along with implications and risks.
Maintenance - Produce a summary of maintenance, implications and likely costs.
Benefits - Detail benefits and reasons for undertaking this scheme i.e.. carbon, CO2, local employment.
DECC rating - Produce an estimated DECC rating with biomass to prove how biomass will improve the DECC rating.
Financial analysis - Detailed financial analysis that includes total capital cost, capital cost per kW and cost per tonne of carbon saved.
Risk assessment - Detail all risks.
Summary - A detailed overview with concise recommendations.

## m2 Feasibility Study
© Biomass Wizard
| Property/Project | [7 empty] | Fuel | Litres | Primary kWh | Boiler eff. | Final kWh
[9 empty] | Oil | 0 | 0 | 0% | 0
| Property m2 |  | 4500 | [6 empty] | 0 | 0 |  | 0
Date
| Job number | [7 empty] | Oil / Litres / Year | 0 |  | £ Oil / Year | 0
| Project partners | [7 empty] | Cost of oil / Litre | 0 |  | Litres / Oil / Yr | 0
|  |  | Comments should be welcomed from all project partners | [5 empty] | £ / Oil / Year | 0 |  | £ Oil / Litre | 0
[9 empty] | kWh / Year | 0 |  | kWh / Year | 0
[9 empty] | £ Oil / Year |  | 0
[9 empty] | Oil / litres / Year |  | 0
[9 empty] | Ave. Cost of Oil / Litre |  | 0
[9 empty] | Heating Oil / Litres |  | 0
[9 empty] | kWh |  | 0
[9 empty] | kWh |  | 0
[9 empty] | Heating Oil / Litres |  | 0
[9 empty] | Heating weeks per year |  | 8760 |  | Full Load Equivalent Hours
[9 empty] | Heating weeks per year |  | 0 |  | 0
[9 empty] | Heating days per week |  | 0 |  | Load Factor %
[9 empty] | Heating hours per heating day |  | 0 |  | 0%
School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
[9 empty] | Primary kWh |  | 0
[9 empty] | Final Heating Output |  | 0
100% Biomass Heating & Hot Water | [8 empty] | FLEH |  | 0
Property m2 |  | 4500 | [6 empty] | Boiler Efficiency |  | 0%
[9 empty] | Boiler Size |  | 0
Insulation |  | 80 | Insulation | 45w m2 - Excellent (New Build)
Heating (kW) |  | 360 |  | 60w m2 - Excellent (Retro)
80w m2 - Good (Retro)
100w m2 - Poor (Retro)
Full Load Equivalent Hours |  | 2100 |  | School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Primary Heating kWh |  | 812903.2258
Boiler Efficiency |  | 93% |  | Ave. = 85% - DH = 75%
Final Heating output kWh |  | 756000
Heating kWh/m2 |  | 168
Primary Hot Water kWh |  | 0
Output Hot Water/kWh |  | 0 |  | Ave 4 bedroom house = 3,742 School = 12,000 - 25,000
Hot water kW |  | 0
Total boiler size |  | 360
Boiler size |  | 360
to be installed
Total Boiler Size Required |  | 360 | kW Installed |  | 360 | % required boiler size |  | 100%
100% Biomass Heatring & Hot Water
Total Heating |  | 812903.2258
Primary kWh
Total Heating |  | 756000
Output kWh
Total Hot Water |  | 0
Primary kWh
Total Hot Water |  | 0
Output kWh
Total Primary |  | 812903.2258
kWh
Total Output |  | 756000
kWh
Boiler size kW |  | 360
Buffer Vessel Sizing
Boiler size kW |  | 360
Litres/kW |  | 15 |  | Optimum size 15-20 litres per kW
Buffer Vessel/litres |  | 5400
20-100 litres/kW - Specialist assessment is required to correctly specifiy boiler and buffer vessel sizing
Fuel Requirements
[5 empty] | P30 W30 chip |  | 6.4701
tonnes/week/winter
P30 W30 chip |  | 232.9236 |  |  | P30 W30 chip |  | 28.76
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 80
P30 W30 chip |  | 1035.2158 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 2.7816
Winter supply/weeks
[5 empty] | P30 W30 NCH Chip |  | 6.8426
tonnes/week/winter
P30 W30 NCH Chip |  | 246.3343 |  |  | P30 W30 chip |  | 30.42
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 80
P30 W30 NCH Chip |  | 755.6267 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 2.6298
Winter supply/weeks
[5 empty] | Pellets |  | 4.8249
tonnes/week/winter
Pellets |  | 173.6973 |  |  | Pellets |  | 7.24
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 80
Pellets |  | 260.4157 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 11.0497
Winter supply/weeks
CO2 Comparison
Gas |  | 150.3871 |  |  | Heating Oil |  | 204.0387
CO2/tonnes/Year |  |  |  |  | CO2/tonnes/Year
Woodfuel |  | 20.3226 |  |  | Woodfuel |  | 20.3226
CO2/tonnes/Year |  |  |  |  | CO2/tonnes/Year
CO2 tonnes/year |  | 130.0645 |  |  | CO2 tonnes/year |  | 183.7161
Saving over gas |  |  |  |  | Saving over oil
Check List |  | Suitable | Unsuitable | Modification | New | Not
|  |  |  | required |  | necessary
|  | y/n | y/n | y/n | y/n | y/n
Boiler house location
Fuel store location
Piping routes
Fuel store size
Log storage
Lorry access
Electric supply
Water supply
Heating system
Building Heat Loss Assessment
BMS
Controls - Weather compensation
Controls - Optimun start/stop
Zoning
Notes
Fuel choice, boiler house & fuel store |  |  |  | Boiler house & fuel store
Check List |  | y/n |  | Check List |  | y/n
Woodchip boiler |  |  |  | New boiler house
Wood Pellet boiler |  |  |  | New fuel store
Miscanthus Pellet boiler |  |  |  | Best site location *
Log boiler |  |  |  | New Access Road
Microgeneration Certificate
Notes
Fuel delivery method/s |  |  |  | Notes
Check List |  |  | y/n
Above ground
Below ground
Walking floor
Hook-bin
Tipped delivery
* Blown delivery
Walking floor & auger
Sweep collector
Auger feed & angled floor
Sweep arm recoil switch
* Always include blown delivery
Check List |  |  | y/n | Notes
Asbestos removal
Buffer vessels
Flue
Flue fan
Ceramic flue filter
Heat meters
Solar heating
RHI
SALEX
Check List |  |  | y/n | Notes
Fuel store sizing
Sealed fuel store
Delivery pipes/sizing
Correct delivery fittings
Dust extraction
Door/spigot/slats
Ventilation
Fuel door safety cut-off
Fuel site glass
Fuel Store Contents - Ultrasonic Monitoring
Exterior lighting
Heat detector/cut off
Matched door key
Reset instructions
Photographs
Fuel supply
Chipping service
Wood & chip delivery equipment
Chip storage
Permissions & Drawings
Check List |  |  | y/n | Check List |  |  | y/n
Planning Permission |  |  |  | Civil Engineering Drawings
Building Regulations |  |  |  | Piping Drawings
CDM Regulations |  |  |  | System Drawings
Confined Space Regulations |  |  |  | Flow & Return design
EHO Permission |  |  |  | Buffer Vessel/Thermal Storage Design
EIA |  |  |  | Flue Specification / Drawings
Habitat Regulations |  |  |  | Boiler House Synoptic Map
TPO
Archaeology
Notes
Current boiler sizing
|  | Boiler Location |  | kW | Boiler Location |  | kW
0
Oil
boiler size/s
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Oil boilers - kWh is a guide as traditionally boilers were over specified
|  | Boiler Location |  | kW | Boiler Location |  | kW
Gas
boiler size/s
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Gas boilers - kWh is a guide as traditionally boilers were over specified
Electric |  | kWh
kWh |  | 0
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Biomass Boiler |  | 0 |  | kWh |  | 0
Size kW
Boiler sizing based on current boiler sizes should be avoided as traditionally boilers were over specified
Boiler sizing based on current fuel usage
Fuel Usage |  | Year 1 | Old Boiler |  | Final kWh | New Boiler
|  |  | Primary kWh | Boiler eff. |  | Boiler eff. | kW boiler
Oil usage / Litres |  | 30000 | 325500 | 80% | 260400 | 93% | 124
Gas usage / kWh |  | 325500 | 325500 | 80% | 260400 | 93% | 124
Electric usage / kWh |  | 325500 | 325500 | 80% | 260400 | 93% | 124
Boiler Size |  | 372
Notes
Quotation |  | 0 |  |  | kW boiler size
to be installed
360
Final |  | 0
installation cost
A biomass report should be produced alongside this pre-install form . The report should include:
A description of the site and surrounding facilities.
Describe building uses that will have an influence on boiler sizing e.g. sports halls, special temprature needs and kitchens etc.
Describe links with other renewables and any boiler sizing. Include buffer vessel / clorifier with solar coil recommendations.
Limitations and constraints - Deliveries, location of boiler and fuel store, noise and emissions.
A report on existing systems - conditions, life expectancy, maintenance costs, likely replacement.
List existing equipment to be used or replaced.
Existing revenue usage - Detailed analysis of existing running costs, including fuel.
A proposed biomass strategy - Include other renewables such as solar water heating, reduction in load from increased thermal insulation or fabric changes, use of buffer vessels. Create a summer water heating and low-load strategy. Outline proposed biomass boiler sizing with justification in terms of heat loads and boiler sizing. Create controls and zoning.
Estimated capital costs - Produce a summary of estimated capital costs with assumptions and an overview of all components and capital costs.
Plans/site layout - Show proposed location of boiler/s and fuel storage, layout of heating mains and district heating layout with accurate measurements. Layout of deliveries, access, reversing and parking.
Links with other projects - Review any projects likely to happen within the short-term (1-2 yrs), medium (2-5 yrs) and long-term (5yrs+) along with implications and risks.
Maintenance - Produce a summary of maintenance, implications and likely costs.
Benefits - Detail benefits and reasons for undertaking this scheme i.e.. carbon, CO2, local employment.
DECC rating - Produce an estimated DECC rating with biomass to prove how biomass will improve the DECC rating.
Financial analysis - Detailed financial analysis that includes total capital cost, capital cost per kW and cost per tonne of carbon saved.
Risk assessment - Detail all risks.
Summary - A detailed overview with concise recommendations.

## Room m2 - Boiler Sizing
Individual room/building calculator
Only fill in yellow boxes |  |  | m2 | Insulation | Full Load | Boiler | Primary | Hot Water | Final | Heating | Boiler
Room Name | Length | Width |  |  | Equivalent Hours | effciency | kWh | kWh | kWh | kWh/m2 | kW
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
|  |  | 0 |  |  |  | #REF! |  | 0 | 0 | 0
|  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
Heated area (m2) |  |  | 0 | 45w m2 - Excellent (New Build) |  | Ave. 85% - DH 75% | #REF! | 0 | 0 | #DIV/0! | 0
60w m2 - Excellent (Retro)
|  |  |  | 80w m2 - Good (Retro) |  |  |  | Ave 4 bedroom house = 3,742 School = 12,000 - 25,000
|  |  |  | 100w m2 - Poor (Retro) |  |  |  | Litres/kW |  | 15
|  |  |  | Most modern buildings compliant with |  |  |  | Buffer Vessel/litres |  | 0
part L of the building regulations will
require a heat density of 50 - 70 w/m2
|  |  |  | FLEH = School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%) |  |  |  | Optimum Buffer Vessel = 15-20 litres per kW
Specialist assessment is required to correctly specifiy boiler and buffer vessel sizing
Hours per year |  | 8760 | Full Load Operating hours
Heating weeks per year |  | 0 | 0
Heating days per week |  | 0 | Load Factor %
Heating hours per heating day |  | 0 | 0%
School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)

## Building m2 - Boiler Sizes
© Biomass Wizard
Individual building calculator
Only fill in yellow boxes
Heated area (m2) | 4500
Insulation | 67 | Insulation | 45w m2 - Excellent (New Build)
50w m2 - Excellent (Retro)
Heating (kW) | 302 |  | 70w m2 - Good (Retro)
100w m2 - Average (Retro)
Full Load Equivalent Hours (FLEH) | 1400 |  | Ave Full Load Equivalanet Hrs/Yr
School = 14,00 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Boiler efficiency | 75%
Ave. 85% - DH 75%
Heating primary | 563733.3333 |  | Most modern buildings compliant with
energy demand/kWh |  |  | part L of the building regulations will
Heating final | 422800 |  | require a heat density of 50 - 70 w/m2
energy output/kWh
Heating kWh/m2 | 93.9556
Hot water Primary | 33333.3333
energy demand/kWh
Hot water/kWh | 25000 |  | 3,742 kWh
Ave 4 bedroom house
Hot water kW | 18 |  | High School = 25,000 kWh
Primary School = 12,000 kWh
Boiler size kW | 320
Primary energy | 597066.6667
demand/kWh
Boiler output/kWh | 447800
Litres/kW | 20
Buffer Vessel / Litres | 6400
Optimum Buffer Vessel = 15-20 litres per kW
Specialist assessment is required to correctly specifiy boiler and buffer vessel sizing
Calculator
Primary kWh | Final kWh
0 | 0
Boiler eff. | Boiler eff.
85% | 85%
Final kWh | Primary kWh
0 | 0
ft2 | 0
m2 | 0
m2 | 0
ft2 | 0
Hours per year |  | 8760 | Full Load Equivalent Hours
Heating weeks per year |  | 0 | 0
Heating days per week |  | 0 | Load Factor %
Heating hours per heating day |  | 0 | 0%
School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)

## District Heating Study
[5 empty] | 45w m2 - Excellent (New Build) | [5 empty] | Only fill in yellow boxes only
[5 empty] | 60w m2 - Excellent (Retro) | [5 empty] | kWh | 0
Building m2 |  |  |  |  | 80w m2 - Good (Retro)
Insulation |  |  |  | Insulation | 100w m2 - Poor (Retro) | [5 empty] | Fuel | Factor | kWh | CO2 Kg/Yr | CO2 Tonnes/Yr
Full Load Equivalent Hours (FLEH) |  |  |  | Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%) | [6 empty] | Electric | 0.523 | 0 | 0 | 0
Boiler Efficiency | [6 empty] | 0 |  |  |  | Electric (CHP) | 0.295 | 0 | 0 | 0
Hot Water kWh |  |  |  | Ave 4 bedroom house = 3,742 School = 12,000 - 25,000 | [6 empty] | Heating (Gas) Oil | 0.251 | 0 | 0 | 0
Primary kWh |  | 0 |  |  |  |  | Boiler Size | 0 | m2 | 0 | LPG | 0.214 | 0 | 0 | 0
Final Heating Output |  | 0 |  | Fuel Cost |  | Fuel Cost | Primary kWh | 0 | Fuel Cost |  | Natural Gas | 0.185 | 0 | 0 | 0
Boiler Size |  | 0 |  | Tonne / Litre |  | Year | Final Heating Output | 0 | Year |  | Woodfuel /Pellets | 0.025 | 0 | 0 | 0
CW Chip P30 M30 / t |  | 0 |  | 61.8 |  | 0 | CW Chip P30 M30 / t | 0 | 0
NCH Chip P30 M30 / t |  | 0 |  | 56.9 |  | 0 | NCH Chip P30 M30 / t | 0 | 0 |  | Woodchip & Pellet CO2 Savings over Heating Oil
Wood Pellets / t |  | 0 |  | 210 |  | 0 | Wood Pellets / t | 0 | 0
Natural Gas / kWh |  | 0 |  | 0.035 |  | 0 | Natural Gas / kWh | 0 | 0 |  | 0 |  |  |  | kWh
Heating Oil / L |  | 0 |  | 0.53 |  | 0 | Heating Oil / litres | 0 | 0 |  | CO2/tonnes/Saving/Year |  | CO2/tonnes/Saving/20 years |  | Car useage savings/Yr | Equiv. car useage savings x 20 yrs
[15 empty] | Ford Focus 1.6L cars | Ford Focus 1.6L cars
[11 empty] | 0 |  | 0 |  | 0 | 0
45w m2 - Excellent (New Build)
[5 empty] | 60w m2 - Excellent (Retro) | [5 empty] | CO2/m3/Saving/Year |  | CO2/m3/saving/20 years |  | Hot air balloons/Year | Hot air balloons x 20 years
Building m2 |  |  |  |  | 80w m2 - Good (Retro)
Insulation |  |  |  | Insulation | 100w m2 - Poor (Retro) | [5 empty] | 0 |  | 0 |  | 0 | 0
Full Load Equivalent Hours (FLEH) |  |  |  | Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Boiler Efficiency | [6 empty] | & |  |  |  | Woodchip & Pellet CO2 Savings over Natural Gas
Hot Water kWh |  |  |  | Ave 4 bedroom house = 3,742 School = 12,000 - 25,000
Primary kWh |  | 0 |  |  |  |  | Boiler Size | 0 | m2 | 0 | 0 |  |  |  | kWh
Final Heating Output |  | 0 |  | Fuel Cost |  | Fuel Cost | Primary kWh | 0 | Fuel Cost |  | CO2/tonnes/Saving/Year |  | CO2/tonnes/Saving/20 years |  | Car useage savings/Yr | Equiv. car useage savings x 20 yrs
Boiler Size |  | 0 |  | Tonne / Litre |  | Year | Final Heating Output | 0 | Year | [5 empty] | Ford Focus 1.6L cars | Ford Focus 1.6L cars
CW Chip P30 M30 / t |  | 0 |  | 61.8 |  | 0 | CW Chip P30 M30 / t | 0 | 0 |  | 0 |  | 0 |  | 0 | 0
NCH Chip P30 M30 / t |  | 0 |  | 56.9 |  | 0 | NCH Chip P30 M30 / t | 0 | 0
Wood Pellets / t |  | 0 |  | 210 |  | 0 | Wood Pellets / t | 0 | 0 |  | CO2/m3/Saving/Year |  | CO2/m3/saving/20 years |  | Hot air balloons/Year | Hot air balloons x 20 years
Natural Gas / kWh |  | 0 |  | 0.035 |  | 0 | Natural Gas / kWh | 0 | 0
Heating Oil / L |  | 0 |  | 0.5 |  | 0 | Heating Oil / litres | 0 | 0 |  | 0 |  | 0 |  | 0 | 0
45w m2 - Excellent (New Build)
[5 empty] | 60w m2 - Excellent (Retro) | [5 empty] | Ford Focus 1.6L cars
Building m2 |  |  |  |  | 80w m2 - Good (Retro) | [5 empty] | CO2/g/km | Miles/Yr | km/Yr | CO2/t/yr
Insulation |  |  |  | Insulation | 100w m2 - Poor (Retro) | [5 empty] | 159 | 12000 | 19312.128 | 3.0706
Full Load Equivalent Hours (FLEH) |  |  |  | Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Boiler Efficiency | [6 empty] | , &
Hot Water kWh |  |  |  | Ave 4 bedroom house = 3,742 School = 12,000 - 25,000 | [6 empty] | Ford Focus 1.6L cars
Primary kWh |  | 0 |  |  |  |  | Boiler Size | 0 | m2 | 0 | CO2/g/km | Km/Year | Miles/Yr | CO2/t/yr
Final Heating Output |  | 0 |  | Fuel Cost |  | Fuel Cost | Primary kWh | 0 | Fuel Cost |  | 159 | 19312 | 11999.9205 | 3.0706
Boiler Size |  | 0 |  | Tonne / Litre |  | Year | Final Heating Output | 0 | Year
CW Chip P30 M30 / t |  | 0 |  | 61.8 |  | 0 | CW Chip P30 M30 / t | 0 | 0 |  | http://www.vcacarfueldata.org.uk/ved/
NCH Chip P30 M30 / t |  | 0 |  | 56.9 |  | 0 | NCH Chip P30 M30 / t | 0 | 0
Wood Pellets / t |  | 0 |  | 210 |  | 0 | Wood Pellets / t | 0 | 0
Natural Gas / kWh |  | 0 |  | 0.035 |  | 0 | Natural Gas / kWh | 0 | 0
Heating Oil / L |  | 0 |  | 0.5 |  | 0 | Heating Oil / litres | 0 | 0
45w m2 - Excellent (New Build)
60w m2 - Excellent (Retro)
Building m2 |  |  |  |  | 80w m2 - Good (Retro)
Insulation |  |  |  | Insulation | 100w m2 - Poor (Retro)
Full Load Equivalent Hours (FLEH) |  |  |  | Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Boiler Efficiency | [6 empty] | , , &
Hot Water kWh |  |  |  | Ave 4 bedroom house = 3,742 School = 12,000 - 25,000
Primary kWh |  | 0 |  |  |  |  | Boiler Size | 0 | m2 | 0
Final Heating Output |  | 0 |  | Fuel Cost |  | Fuel Cost | Primary kWh | 0 | Fuel Cost
Boiler Size |  | 0 |  | Tonne / Litre |  | Year | Final Heating Output | 0 | Year
CW Chip P30 M30 / t |  | 0 |  | 61.8 |  | 0 | CW Chip P30 M30 / t | 0 | 0
NCH Chip P30 M30 / t |  | 0 |  | 56.9 |  | 0 | NCH Chip P30 M30 / t | 0 | 0
Wood Pellets / t |  | 0 |  | 210 |  | 0 | Wood Pellets / t | 0 | 0
Natural Gas / kWh |  | 0 |  | 0.035 |  | 0 | Natural Gas / kWh | 0 | 0
Heating Oil / L |  | 0 |  | 0.5 |  | 0 | Heating Oil / litres | 0 | 0
45w m2 - Excellent (New Build)
60w m2 - Excellent (Retro)
Building m2 |  |  |  |  | 80w m2 - Good (Retro)
Insulation |  |  |  | Insulation | 100w m2 - Poor (Retro)
Full Load Equivalent Hours (FLEH) |  |  |  | Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Boiler Efficiency | [6 empty] | , , , &
Hot Water kWh |  |  |  | Ave 4 bedroom house = 3,742 School = 12,000 - 25,000
Primary kWh |  | 0 |  |  |  |  | Boiler Size | 0 | m2 | 0
Final Heating Output |  | 0 |  | Fuel Cost |  | Fuel Cost | Primary kWh | 0 | Fuel Cost
Boiler Size |  | 0 |  | Tonne / Litre |  | Year | Final Heating Output | 0 | Year
CW Chip P30 M30 / t |  | 0 |  | 61.8 |  | 0 | CW Chip P30 M30 / t | 0 | 0
NCH Chip P30 M30 / t |  | 0 |  | 56.9 |  | 0 | NCH Chip P30 M30 / t | 0 | 0
Wood Pellets / t |  | 0 |  | 210 |  | 0 | Wood Pellets / t | 0 | 0
Natural Gas / kWh |  | 0 |  | 0.035 |  | 0 | Natural Gas / kWh | 0 | 0
Heating Oil / L |  | 0 |  | 0.5 |  | 0 | Heating Oil / litres | 0 | 0
45w m2 - Excellent (New Build)
60w m2 - Excellent (Retro)
Building m2 |  |  |  |  | 80w m2 - Good (Retro)
Insulation |  |  |  | Insulation | 100w m2 - Poor (Retro)
Full Load Equivalent Hours (FLEH) |  |  |  | Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Boiler Efficiency | [6 empty] | , , , , &
Hot Water kWh |  |  |  | Ave 4 bedroom house = 3,742 School = 12,000 - 25,000
Primary kWh |  | 0 |  |  |  |  | Boiler Size | 0 | m2 | 0
Final Heating Output |  | 0 |  | Fuel Cost |  | Fuel Cost | Primary kWh | 0 | Fuel Cost
Boiler Size |  | 0 |  | Tonne / Litre |  | Year | Final Heating Output | 0 | Year
CW Chip P30 M30 / t |  | 0 |  | 61.8 |  | 0 | CW Chip P30 M30 / t | 0 | 0
NCH Chip P30 M30 / t |  | 0 |  | 56.9 |  | 0 | NCH Chip P30 M30 / t | 0 | 0
Wood Pellets / t |  | 0 |  | 210 |  | 0 | Wood Pellets / t | 0 | 0
Natural Gas / kWh |  | 0 |  | 0.035 |  | 0 | Natural Gas / kWh | 0 | 0
Heating Oil / L |  | 0 |  | 0.5 |  | 0 | Heating Oil / litres | 0 | 0
Fuel | Litres | Primary kWh | Boiler eff. | Final kWh
Oil | 0 | 0 | 0% | 0
| 0 | 0 |  | 0
Oil / Litres / Year |  | 25000
Cost of oil / Litre |  | 0.5 |  | Month | Yearly % | kWh
£ / Oil / Year |  | 12500 |  | January | 13.5% | 0
kWh / Year |  | 271250 |  | February | 14% | 0
|  |  |  | March | 10% | 0
£ Oil / Year |  | 12500 |  | April | 7% | 0
Litres / Oil / Yr |  | 25000 |  | May | 4% | 0
£ Oil / Litre |  | 0.5 |  | June | 3% | 0
kWh / Year |  | 271250 |  | July | 3% | 0
|  |  |  | August | 4% | 0
Heating Oil / litres |  | 0 |  | September | 8.5% | 0
kWh |  | 0 |  | October | 10% | 0
|  |  |  | November | 11% | 0
kWh |  | 0 |  | December | 12% | 0
Heating Oil / litres |  | 0 |  |  | 100% | 0
Heating weeks per year |  | 8760 |  | Total kWh |  | 0
Heating weeks per year |  | 0 |  | Monthly kWh |  | 0
Heating days per week |  | 0 |  | % of Total Cost |  | #DIV/0!
Heating hours/ per day |  | 0
Full Load Equivalent Hours |  |  |  | Total kWh |  | 0
0 |  |  |  | Montly kWh |  | 0
Load Factor % |  |  |  | % of Total Cost |  | #DIV/0!
0%
School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)

## kW Feasibility Study
© Biomass Wizard
| Property/Project | [7 empty] | Fuel | Litres | Primary kWh | Boiler eff. | Final kWh
[9 empty] | Oil | 0 | 0 | 0% | 0
| Boiler Size / kW |  | 150 | [6 empty] | 0 | 0 |  | 0
| Date |  | 2011-11-29
| Job number | [7 empty] | Oil / Litres / Year | 0 |  | £ Oil / Year | 0
| Project partners | [7 empty] | Cost of oil / Litre | 0 |  | Litres / Oil / Yr | 0
|  |  | Comments should be welcomed from all project partners | [5 empty] | £ / Oil / Year | 0 |  | £ Oil / Litre | 0
[9 empty] | kWh / Year | 0 |  | kWh / Year | 0
[9 empty] | £ Oil / Year |  | 0
[9 empty] | Oil / litres / Year |  | 0
[9 empty] | Ave. Cost of Oil / Litre |  | 0
[9 empty] | Heating Oil / Litres |  | 0
[9 empty] | kWh |  | 0
[9 empty] | kWh |  | 0
[9 empty] | Heating Oil / Litres |  | 0
[9 empty] | Heating weeks per year |  | 8760 |  | Full Load Equivalent Hours
[9 empty] | Heating weeks per year |  | 0 |  | 0
[9 empty] | Heating days per week |  | 0 |  | Load Factor %
[9 empty] | Heating hours per heating day |  | 0 |  | 0%
School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
[9 empty] | Primary kWh |  | #DIV/0!
[9 empty] | Final Heating Output |  | 0
% Biomass Heating & Hot Water | [8 empty] | Full Load Equivalent Hours |  | 0
Heating (kW) |  | 150 | [6 empty] | Boiler Efficiency |  | 0%
[9 empty] | Boiler Size |  | 0
Full Load Equivalent Hours |  | 2100 |  | School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Primary Heating kWh |  | 338709.6774
Boiler Efficiency |  | 93% |  | Ave. = 85% - DH = 75%
Final Heating output kWh |  | 315000
Primary Hot Water kWh |  | 0
Output Hot Water/kWh |  | 0 |  | Ave 4 bedroom house = 3,742 High School = 25,000
Hot water kW |  | 0
Total boiler size |  | 150
Boiler size |  | 150
to be installed
Total Boiler Size Required |  | 150 | kW Installed |  | 150 | % required boiler size |  | 100%
100% Biomass Heating & Hot Water
Total Heating |  | 338709.6774
Primary kWh
Total Heating |  | 315000
Output kWh
Total Hot Water |  | 0
Primary kWh
Total Hot Water |  | 0
Output kWh
Total Primary |  | 338709.6774
kWh
Total Output |  | 315000
kWh
Boiler size kW |  | 150
Buffer Vessel Sizing
Boiler size kW |  | 150
Litres/kW |  | 15 |  | Optimum size 15-20 litres per kW
Buffer Vessel/litres |  | 2250
20-100 litres/kW - Specialist assessment is required to correctly specifiy boiler and buffer vessel sizing
Fuel Requirements
[5 empty] | P30 W30 chip |  | 2.6959
tonnes/week/winter
P30 W30 CW Chip |  | 97.0515 |  |  | P30 W30 chip |  | 11.99
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 40
P30 W30 CW Chip |  | 431.3399 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 3.3361
Winter supply/weeks
[5 empty] | P30 W30 NCH Chip |  | 2.8511
tonnes/week/winter
P30 W30 NCH Chip |  | 102.6393 |  |  | P30 W30 chip |  | 12.68
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 40
P30 W30 NCH Chip |  | 314.8445 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 3.1546
Winter supply/weeks
[5 empty] | Pellets |  | 2.0104
tonnes/week/winter
Pellets |  | 72.3739 |  |  | Pellets |  | 3.02
tonnes/year |  |  |  |  | m3/week/winter
[5 empty] | Fuel store size |  | 40
Pellets |  | 108.5065 |  |  | m3
m3/year |  |  |  |  | Fuel store |  | 13.245
Winter supply/weeks
CO2 Comparison
Gas |  | 62.6613 |  |  | Heating Oil |  | 85.0161
CO2/tonnes/Year |  |  |  |  | CO2/tonnes/Year
Woodfuel |  | 8.4677 |  |  | Woodfuel |  | 8.4677
CO2/tonnes/Year |  |  |  |  | CO2/tonnes/Year
CO2 tonnes/year |  | 54.1935 |  |  | CO2 tonnes/year |  | 76.5484
Saving over gas |  |  |  |  | Saving over oil
Check List |  | Suitable | Unsuitable | Modification | New | Not
|  |  |  | required |  | necessary
|  | y/n | y/n | y/n | y/n | y/n
Boiler house location |  | y
Fuel store location |  | y
Piping routes |  | y
Fuel store size |  | y
Log storage |  | NA
Lorry access |  | y
Electric supply |  | y
Water supply |  | y
Heating system |  | y
Building Heat Loss Assessment |  | NA
BMS |  | NA
Controls - Weather compensation |  | NA
Controls - Optimun start/stop |  | y
Zoning |  | ?
Notes
Fuel choice, boiler house & fuel store |  |  |  | Boiler house & fuel store
Check List |  | y/n |  | Check List |  | y/n
Woodchip boiler |  | n |  | New boiler house |  | n
Wood Pellet boiler |  | y |  | New fuel store |  | y
Miscanthus Pellet boiler |  | n |  | Best site location * |  | y
Log boiler |  | n |  | New Access Road |  | y
Microgeneration Certificate |  | y
Notes
Fuel delivery method/s |  |  |  | Notes
Check List |  |  | y/n
Above ground |  |  | y
Below ground |  |  | n
Walking floor |  |  | n
Hook-bin |  |  | n
Tipped delivery |  |  | n
* Blown delivery |  |  | y
Walking floor & auger |  |  | n
Sweep collector |  |  | ?
Auger feed & angled floor |  |  | ?
Sweep arm recoil switch |  |  | y
* Always include blown delivery
Check List |  |  | y/n | Notes
Asbestos removal |  |  | n
Buffer vessels |  |  | y
Flue |  |  | y
Flue fan |  |  | n
Ceramic flue filter |  |  | n
Heat meters |  |  | y
Solar heating |  |  | n
RHI |  |  | y
SALEX |  |  | n
Check List |  |  | y/n | Notes
Fuel store sizing |  |  | y
Sealed fuel store |  |  | y
Delivery pipes/sizing |  |  | y
Correct delivery fittings |  |  | y
Dust extraction |  |  | n
Door/spigot/slats |  |  | y
Ventilation |  |  | n
Fuel door safety cut-off |  |  | n
Fuel site glass |  |  | n
Fuel Store Contents - Ultrasonic Monitoring |  |  | y
Exterior lighting |  |  | y
Heat detector/cut off |  |  | n
Matched door key |  |  | n
Reset instructions |  |  | y
Photographs |  |  | n
Fuel supply |  |  | y
Chipping service |  |  | NA
Wood & chip delivery equipment |  |  | NA
Chip storage |  |  | NA
Permissions & Drawings
Check List |  |  | y/n | Check List |  |  | y/n
Planning Permission |  |  | ? | Civil Engineering Drawings |  |  | NA
Building Regulations |  |  | ? | Piping Drawings |  |  | y
CDM Regulations |  |  | ? | System Drawings |  |  | y
Confined Space Regulations |  |  | NA | Flow & Return design |  |  | y
EHO Permission |  |  | n | Buffer Vessel/Thermal Storage Design |  |  | y
EIA |  |  | n | Flue Specification / Drawings |  |  | y
Habitat Regulations |  |  | NA | Boiler House Synoptic Map |  |  | y
TPO |  |  | ?
Archaeology |  |  | ?
Notes
Current boiler sizing
|  | Boiler Location |  | kW | Boiler Location |  | kW
|  |  |  | 0 |  |  | 0
Oil |  |  |  | 0 |  |  | 0
boiler size/s |  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Oil boilers - kWh is a guide as traditionally boilers were over specified
|  | Boiler Location |  | kW | Boiler Location |  | kW
|  |  |  | 0 |  |  | 0
Gas |  |  |  | 0 |  |  | 0
boiler size/s |  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Gas boilers - kWh is a guide as traditionally boilers were over specified
Electric |  | kWh
kWh |  | 0
Total boiler sizes |  | 0 |  | kW | 0 |  | kWh
Biomass Boiler |  | 0 |  | kWh |  | 0
Size kW
Boiler sizing based on current boiler sizes should be avoided as traditionally boilers were over specified
Boiler sizing based on current fuel usage
Fuel Usage |  | Year 1 | Old Boiler |  | Final kWh | New Boiler
|  |  | Primary kWh | Boiler eff. |  | Boiler eff. | kW boiler
Oil usage / Litres |  | 30000 | 325500 | 80% | 260400 | 93% | 124
Gas usage / kWh |  | 325500 | 325500 | 80% | 260400 | 93% | 124
Electric usage / kWh |  | 325500 | 325500 | 80% | 260400 | 93% | 124
Boiler Size |  | 372
Notes
Quotation |  | 0 |  |  | kW boiler size
to be installed
150
Final |  | 0
installation cost
A biomass report should be produced alongside this pre-install form . The report should include:
A description of the site and surrounding facilities.
Describe building uses that will have an influence on boiler sizing e.g. sports halls, special temprature needs and kitchens etc.
Describe links with other renewables and any boiler sizing. Include buffer vessel / clorifier with solar coil recommendations.
Limitations and constraints - Deliveries, location of boiler and fuel store, noise and emissions.
A report on existing systems - conditions, life expectancy, maintenance costs, likely replacement.
List existing equipment to be used or replaced.
Existing revenue usage - Detailed analysis of existing running costs, including fuel.
A proposed biomass strategy - Include other renewables such as solar water heating, reduction in load from increased thermal insulation or fabric changes, use of buffer vessels. Create a summer water heating and low-load strategy. Outline proposed biomass boiler sizing with justification in terms of heat loads and boiler sizing. Create controls and zoning.
Estimated capital costs - Produce a summary of estimated capital costs with assumptions and an overview of all components and capital costs.
Plans/site layout - Show proposed location of boiler/s and fuel storage, layout of heating mains and district heating layout with accurate measurements. Layout of deliveries, access, reversing and parking.
Links with other projects - Review any projects likely to happen within the short-term (1-2 yrs), medium (2-5 yrs) and long-term (5yrs+) along with implications and risks.
Maintenance - Produce a summary of maintenance, implications and likely costs.
Benefits - Detail benefits and reasons for undertaking this scheme i.e.. carbon, CO2, local employment.
DECC rating - Produce an estimated DECC rating with biomass to prove how biomass will improve the DECC rating.
Financial analysis - Detailed financial analysis that includes total capital cost, capital cost per kW and cost per tonne of carbon saved.
Risk assessment - Detail all risks.
Summary - A detailed overview with concise recommendations.

## Heating Oil Sizing - Costs
© Biomass Wizard | [5 empty] | Primary kWh |  | Fuel | Litres | Primary kWh | Boiler eff. | Final kWh
Heating Oil Boiler Sizing | [5 empty] | 0 |  | Oil | 200000 | 2170000 | 75% | 1627500
Litres of oil used per year | [5 empty] | Boiler eff. |  |  | 200000 | 2170000 |  | 1627500
© | [5 empty] | 0%
Oil use per year £ | 25000 |  |  |  |  | Final kWh |  | Oil / Litres / Year | 34000 |  | £ Oil / Year | 17000
Cost of oil per litre | 0.5 |  |  |  |  | 0 |  | Cost of oil / Litre | 0.5 |  | Litres / Oil / Yr | 34000
Oil used per yr/l | 50000 |  |  |  |  | Final kWh |  | £ / Oil / Year | 17000 |  | £ Oil / Litre | 0.5
kWh/yr | 542500 |  |  |  |  | 0 |  | kWh / Year | 368900 |  | kWh / Year | 368900
Old boiler - How much energy used - Taking into account boiler efficiencies | [5 empty] | Boiler eff.
© | [5 empty] | 0% |  | Heating Oil / Litres |  | 0
Primary Heat Demand kWh/yr | 542500 |  |  |  |  | Primary kWh |  | kWh |  | 0
Old boiler/eff. % | 80% | 70%-85% |  |  |  | #DIV/0!
Final Heat Demand kWh/yr | 434000 | [6 empty] | kWh |  | 0
Full Load Equivalent Hours | 1800 |  |  |  |  | CW P30 M30 - Tonnes/m3 Price Conversion |  | Heating Oil / Litres |  | 0
|  | School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%) |  |  |  | Tonnes | 1
Boiler size kW | 242 |  |  |  |  | m3 | 4.4444 | Heating weeks per year |  | 8760 |  | Full Load Equivalent Hours
New boiler size - Taking into account boiler efficiencies and annual utilisation rate | [5 empty] | £ / tonne CW chip P30 M30 | 44.95 | Heating weeks per year |  | 0 |  | 0
© | [5 empty] | £ / m3 CW chip P30 M30 | 10.1138 | Heating days per week |  | 0 |  | Load Factor %
Primary Heat Demand kWh/yr | 510588.2353 | New boiler kWh of old boiler kWh |  | 94.12% |  | Fuel Cost | 44.95 | Heating hours per heating day |  | 0 |  | 0%
Final Heat Demand kWh/yr | 434000 | [6 empty] | School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Full Load Equivalent Hours | 1800 | School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%) |  |  |  | CW P30 M30 - m3/Tonnes Price Conversion |  | Primary kWh |  | #DIV/0!
[6 empty] | m3 | 1 | Final Heating Output |  | 0
New boiler eff. | 85% | Approx. 85% |  |  |  | Tonnes | 0.225 | Full Load Equivalent Hours |  | 0
Boiler Size/kW | 242 |  |  |  |  | £ / m3 CW chip P30 M30 | 10.11 | Boiler Efficiency |  | 0%
[6 empty] | £ / tonne CW chip P30 M30 | 44.9333 | Boiler Size |  | #DIV/0!
[6 empty] | Fuel Cost | 10.11 | CW - M30 - Woodchip production comparisons
[8 empty] | Only alter yellow boxes |  |  |  | CW P30 M55
Litres/kW | 15 | Optimum size 15-20 litres per kW |  |  |  | NCH P30 M30 - Tonnes/m3 Price Conversion |  | Woodfuel costs |  | £/tonne | Buying-in wood | Tonnes | m3
Buffer Vessel/litres | 3630 |  |  |  |  | Tonnes | 1 | 1 tonne timber value @ M55 |  | 8 | 32 | 1 | 1.1455
[6 empty] | m3 | 3.0675 | Timber value @ M30 |  | 12.4494 | 49.7977 | 0.873 | 1
[6 empty] | £ / tonne NCH chip P30 M30 | 52.37 | Harvest/Extract |  | 15 | 0 | CW P30 M30
20-100 litres/kW - Specialist assessment is required to correctly specifiy boiler and buffer vessel sizing | [5 empty] | £ / m3 NCH chip P30 M30 | 17.0726 | Haulage to depot |  | 8 | 0 | Tonnes | m3
Energy produced | [5 empty] | Fuel Cost | 52.37 | Chipping |  | 7.5 | 7.5 | 1 | 4.4444
© | Primary kWh Demand | Final kWh Demand | [5 empty] | Handling/Storage/Admin |  | 2 | 2 | 0.227 | 1
kWh/Yr | 510588.2353 | 434000 |  |  |  | NCH P30 M30 - m3/Tonnes Price Conversion |  | Delivery |  | 0 | 0
MWh/Yr | 510.5882 | 434 |  |  |  | m3 | 3.0675 | Actual total |  | 44.9494 | 59.2977
MJ/Yr | 1838117.6471 | 1562400 |  |  |  | Tonnes | 1 | % Profit |  | 0% | 0%
GJ/Yr | 1838.1176 | 1562.4 |  |  |  | £ / m3 NCH chip P30 M30 | 34.23 | Total |  | 44.9494 | 59.2977
BTU | 1742127058.8235 | 1480808000 |  |  |  | £ / tonne NCH chip P30 M30 | 105 | NCH - M30 - Woodchip production comparisons
Boiler fuel requirement - Tonnes/yr | [5 empty] | Fuel Cost | 105.0005 | Only alter yellow boxes |  |  |  | NCH P30 M55
© | [7 empty] | Woodfuel costs |  | £/tonne | Buying-in wood | Tonnes | m3
Fuel Requirements | kWh | kWh/tonne | Tonnes/yr |  |  | W-Pellets - Tonnes/m3 Price Conversion |  | 1 tonne timber value @ M55 |  | 12 | 48 | 1 | 0.78989
CW chip P30 M30 | 510588.2353 | 3490 | 146.3004 |  |  | Tonnes | 1 | Timber value @ M30 |  | 12.87 | 51.4801 | 1.266 | 1
NCH chip P30 M30 | 510588.2353 | 3300 | 154.7237 |  |  | m3 | 1.4993 | Harvest/Extract |  | 20 | 0 | NCH P30 M30
Miscanthus Pellets | 510588.2353 | 4361 | 117.0805 |  |  | £ / tonne Pellets | 210 | Haulage to depot |  | 8.5 | 0 | Tonnes | m3
Wood Pellets | 510588.2353 | 4680 | 109.1001 |  |  | £ / m3 Pellets | 140.07 | Chipping |  | 9 | 9 | 1 | 3.0675
Boiler fuel requirement - m3/yr | [5 empty] | Fuel Cost | 210 | Handling/Storage/Admin |  | 2 | 2 | 0.326 | 1
© | [7 empty] | Delivery |  | 0 | 0
Fuel Requirements | Tonnes/yr | kg/M3 | m3 |  |  | W-Pellets - m3/Tonnes Price Conversion |  | Actual total |  | 52.37 | 62.4801
CW chip P30 W30 | 146.3004 | 225 | 650.2238 |  |  | m3 | 1.4993 | % Profit |  | 0% | 0%
NCH chip P30 W30 | 154.7237 | 326 | 474.6126 |  |  | Tonnes | 1 | Total |  | 52.37 | 62.4801
Miscanthus Pellets | 117.0805 | 650 | 180.1239 |  |  | Pellets/m3 | 133.4
Wood Pellets | 109.1001 | 667 | 163.5683 |  |  | £ / Pellets / tonne | 200
Boiler fuel costs - £ per tonne/per year | [5 empty] | Fuel Cost | 200.0066
Woodchip/Tonne | © |  |  | Pence / kWh
Natural Gas/kwh | 0.035 | Fuel Cost/year | 17870.5882 | 4.1176 | 0.035 | M-Pellets - Tonnes/m3 Price Conversion
Heating (Gas) Oil/litre | 0.5 | Fuel Cost/year | 24666.0983 | 5.6834 | 0.5 | Tonnes | 1
CW chip P30 M30/tonne | 44.95 | Fuel Cost/year | 6576.2009 | 1.5153 | 44.95 | m3 | 1.5385
NCH chip P30 M30/tonne | 52.37 | Fuel Cost/year | 8102.8806 | 1.867 | 52.37 | £ / tonne Pellets | 180
Miscanthus Pellets/tonne | 180 | Fuel Cost/year | 21074.4972 | 4.8559 | 180 | £ / m3 Pellets | 117
Wood Pellets/tonne | 210 | Fuel Cost/year | 22911.0106 | 5.279 | 210 | Fuel Cost | 180 | [6 empty] | Energy type | kWh | kg CO2/kWh | Tonnes CO2 | Reference
Boiler fuel costs - £ per m3/per year | [13 empty] | Electricity (Grid) | 510588.2353 | 0.523 | 267.0366 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 3
Woodchip/m3 | © |  |  | Pence / kWh |  | M-Pellets - m3/Tonnes Price Conversion | [7 empty] | Electricity - CHP | 510588.2353 | 0.295 | 150.6235 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 3
Natural Gas/kwh | 0.035 | Fuel Cost/year | 17870.5882 | 4.1176 | 0.035 | m3 | 1.5385 | [6 empty] | Heating (Gas) Oil | 510588.2353 | 0.25146 | 128.3925 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 1
Heating (Gas) Oil/litre | 0.5 | Fuel Cost/year | 24666.0983 | 5.6834 | 0.5 | Tonnes | 1 | [6 empty] | LPG | 510588.2353 | 0.21419 | 109.3629 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 1
CW chip P30 M30/m3 | 10.12 | Fuel Cost/year | 6580.265 | 1.5162 | 10.12 | Pellets / m3 | 117 | [6 empty] | Natural Gas | 510588.2353 | 0.18497 | 94.4435 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 1
NCH chip P30 M30/m3 | 17.08 | Fuel Cost/year | 8106.3832 | 1.8678 | 17.08 | £ / Pellets/tonne | 180 | [6 empty] | Wood & Pellets | 510588.2353 | 0.025 | 12.7647 | 0.025 kgCO2/kWh provided in SAP2005, Table 12.
Miscanthus Pellets/m3 | 117 | Fuel Cost/year | 21074.4972 | 4.8559 | 117 | Fuel Cost | 180.0045 | [6 empty] | Coal | 510588.2353 | 0.32886 | 167.912 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 1
Wood Pellets/m3 | 140.07 | Fuel Cost/year | 22911.0106 | 5.279 | 140.07
One Year CO2 Saving over
Heating (Gas) Oil/tonnes
115.6278
20 year CO2 saving over
Heating (Gas) Oil/tonnes
2312.5562

## kWh Boiler Sizing - Costs
© Biomass Wizard | [5 empty] | Primary kWh |  | Fuel | Litres | Primary kWh | Boiler eff. | Final kWh
kWh Output Sizing | [5 empty] | 0 |  | Oil | 200000 | 2170000 | 75% | 1627500
Output kWh/yr | 147000 |  |  |  |  | Boiler eff. |  |  | 200000 | 2170000 |  | 1627500
0%
[6 empty] | Final kWh |  | Oil / Litres / Year | 34000 |  | £ Oil / Year | 17000
Old boiler/eff. % | 85% |  | 70%-85% |  |  | 0 |  | Cost of oil / Litre | 0.5 |  | Litres / Oil / Yr | 34000
Primary Energy kWh/yr | 172941.1765 |  |  |  |  | Final kWh |  | £ / Oil / Year | 17000 |  | £ Oil / Litre | 0.5
Energy produced | [5 empty] | 0 |  | kWh / Year | 368900 |  | kWh / Year | 368900
© | Primary kWh Demand | Final kWh Demand |  |  |  | Boiler eff.
kWh/Yr | 172941.1765 | 172941.1765 |  |  |  | 0% |  | Heating Oil / Litres |  | 0
MWh/Yr | 172.9412 | 172.9412 |  |  |  | Primary kWh |  | kWh |  | 0
MJ/Yr | 622588.2353 | 622588.2353 |  |  |  | #DIV/0!
GJ/Yr | 622.5882 | 622.5882 | [5 empty] | kWh |  | 0
BTU | 590075294.1176 | 590075294.1176 |  |  |  | CW P30 M30 - Tonnes/m3 Price Conversion |  | Heating Oil / Litres |  | 0
New boiler size - Taking into account boiler efficiencies and annual utilisation rate | [5 empty] | Tonnes | 1
© | [5 empty] | m3 | 4.4444 | Heating weeks per year |  | 8760 |  | Full Load Equivalent Hours
Primary Energy kWh/yr | 172941.1765 | New boiler kWh of old boiler kWh |  | 100% |  | £ / tonne CW chip P30 M30 | 90 | Heating weeks per year |  | 0 |  | 0
Final kWh/Yr | 147000 |  |  |  |  | £ / m3 CW chip P30 M30 | 20.25 | Heating days per week |  | 0 |  | Load Factor %
Full Load Equivalent Hours | 1800 | School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%) |  |  |  | Fuel Cost | 90 | Heating hours per heating day |  | 0 |  | 0%
School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
New boiler eff. | 85% | Approx. 85% |  |  |  | CW P30 M30 - m3/Tonnes Price Conversion |  | Primary kWh |  | #DIV/0!
Boiler size | 82 |  |  |  |  | m3 | 1 | Final Heating Output |  | 0
[6 empty] | Tonnes | 0.225 | Full Load Equivalent Hours |  | 0
[6 empty] | £ / m3 CW chip P30 M30 | 20.25 | Boiler Efficiency |  | 0%
[6 empty] | £ / tonne CW chip P30 M30 | 90 | Boiler Size |  | #DIV/0!
Litres/kW | 15 | Optimum size 15-20 litres per kW |  |  |  | Fuel Cost | 20.25 | CW - M30 - Woodchip production comparisons
Buffer Vessel/litres | 1230 | [6 empty] | Only alter yellow boxes |  |  |  | CW P30 M55
[6 empty] | NCH P30 M30 - Tonnes/m3 Price Conversion |  | Woodfuel costs |  | £/tonne | Buying-in wood | Tonnes | m3
[6 empty] | Tonnes | 1 | 1 tonne timber value @ M55 |  | 8 | 32 | 1 | 1.1455
20-100 litres/kW - Specialist assessment is required to correctly specifiy boiler and buffer vessel sizing | [5 empty] | m3 | 3.0675 | Timber value @ M30 |  | 12.4494 | 49.7977 | 0.873 | 1
Boiler fuel requirement - Tonnes/yr | [5 empty] | £ / tonne NCH chip P30 M30 | 105 | Harvest/Extract |  | 15 | 0 | CW P30 M30
© | [5 empty] | £ / m3 NCH chip P30 M30 | 34.23 | Haulage to depot |  | 8 | 0 | Tonnes | m3
Fuel - Under 900 kW boilers | kWh | kWh/tonne | Tonnes/yr |  |  | Fuel Cost | 105 | Chipping |  | 7.5 | 7.5 | 1 | 4.4444
CW chip P30 M30 | 172941.1765 | 3490 | 49.5533 |  |  |  |  | Handling/Storage/Admin |  | 2 | 2 | 0.227 | 1
NCH chip P30 M30 | 172941.1765 | 3300 | 52.4064 |  |  | NCH P30 M30 - m3/Tonnes Price Conversion |  | Delivery |  | 0 | 0
Miscanthus Pellets | 172941.1765 | 4361 | 39.6563 |  |  | m3 | 3.0675 | Actual total |  | 44.9494 | 59.2977
Wood Pellets | 172941.1765 | 4680 | 36.9532 |  |  | Tonnes | 1 | % Profit |  | 0% | 0%
[6 empty] | £ / m3 NCH chip P30 M30 | 34.23 | Total |  | 44.9494 | 59.2977
Boiler fuel requirement - m3/yr | [5 empty] | £ / tonne NCH chip P30 M30 | 105 | NCH - M30 - Woodchip production comparisons
Fuel Requirements | Tonnes/yr | kg/m3 | m3 |  |  | Fuel Cost | 105.0005 | Only alter yellow boxes |  |  |  | NCH P30 M55
CW chip P30 M30 | 49.5533 | 225 | 220.2371 |  |  |  |  | Woodfuel costs |  | £/tonne | Buying-in wood | Tonnes | m3
NCH chip P30 M30 | 52.4064 | 326 | 160.7559 |  |  | W-Pellets - Tonnes/m3 Price Conversion |  | 1 tonne timber value @ M55 |  | 12 | 48 | 1 | 0.78989
Miscanthus Pellets | 39.6563 | 650 | 61.0097 |  |  | Tonnes | 1 | Timber value @ M30 |  | 12.87 | 51.4801 | 1.266 | 1
Wood Pellets | 36.9532 | 667 | 55.4022 |  |  | m3 | 1.4993 | Harvest/Extract |  | 20 | 0 | NCH P30 M30
[6 empty] | £ / tonne Pellets | 200 | Haulage to depot |  | 8.5 | 0 | Tonnes | m3
Woodchip/Tonne | © |  |  | Pence / kWh |  | £ / m3 Pellets | 133.4 | Chipping |  | 9 | 9 | 1 | 3.0675
Natural Gas/kwh | 0.035 | Fuel Cost/year | 6052.9412 | 4.1176 | 0.035 | Fuel Cost | 200 | Handling/Storage/Admin |  | 2 | 2 | 0.326 | 1
Heating (Gas) Oil/litre | 0.5 | Fuel Cost/year | 7969.6395 | 5.4215 | 0.5 |  |  | Delivery |  | 0 | 0
CW chip P30 M30/tonne | 44.95 | Fuel Cost/year | 2227.4229 | 1.5153 | 44.95 | W-Pellets - m3/Tonnes Price Conversion |  | Actual total |  | 52.37 | 62.4801
NCH chip P30 M30/tonne | 52.37 | Fuel Cost/year | 2744.5241 | 1.867 | 52.37 | m3 | 1.4993 | % Profit |  | 0% | 0%
Miscanthus Pellets/tonne | 180 | Fuel Cost/year | 7138.1362 | 4.8559 | 180 | Tonnes | 1 | Total |  | 52.37 | 62.4801
Wood Pellets/tonne | 210 | Fuel Cost/year | 7760.181 | 5.279 | 210 | Pellets/m3 | 133.4
[6 empty] | £ / Pellets / tonne | 200
Woodchip/m3 | © |  |  | £ / kWh |  | Fuel Cost | 200.0066
Natural Gas/kwh | 0.035 | Fuel Cost/year | 6052.9412 | 4.1176 | 0.035
Heating (Gas) Oil/litre | 0.5 | Fuel Cost/year | 7969.6395 | 5.4215 | 0.5 | M-Pellets - Tonnes/m3 Price Conversion
CW chip P30 M30/m3 | 10.12 | Fuel Cost/year | 2228.7994 | 1.5162 | 10.12 | Tonnes | 1
NCH chip P30 M30/m3 | 17.08 | Fuel Cost/year | 2745.7104 | 1.8678 | 17.08 | m3 | 1.5385
Miscanthus Pellets/m3 | 117 | Fuel Cost/year | 7138.1362 | 4.8559 | 117 | £ / tonne Pellets | 180
Wood Pellets/m3 | 140.07 | Fuel Cost/year | 7760.181 | 5.279 | 140.07 | £ / m3 Pellets | 117
[6 empty] | Fuel Cost | 180 | [6 empty] | Energy type | kWh | kg CO2/kWh | Tonnes CO2 | Reference
[14 empty] | Electricity (Grid) | 172941.1765 | 0.523 | 90.4479 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 3
[6 empty] | M-Pellets - m3/Tonnes Price Conversion | [7 empty] | Electricity - CHP | 172941.1765 | 0.295 | 51.0176 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 3
[6 empty] | m3 | 1.5385 | [6 empty] | Heating (Gas) Oil | 172941.1765 | 0.251 | 43.4082 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 1
[6 empty] | Tonnes | 1 | [6 empty] | LPG | 172941.1765 | 0.21419 | 37.0423 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 1
[6 empty] | Pellets / m3 | 117 | [6 empty] | Natural Gas | 172941.1765 | 0.18497 | 31.9889 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 1
[6 empty] | £ / Pellets/tonne | 180 | [6 empty] | Wood & Pellets | 172941.1765 | 0.025 | 4.3235 | 0.025 kgCO2/kWh provided in SAP2005, Table 12.
[6 empty] | Fuel Cost | 180.0045 | [6 empty] | Coal | 172941.1765 | 0.32886 | 56.8734 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 1
One Year CO2 Saving over
Heating (Gas) Oil/tonnes
39.0847
20 year CO2 saving over
Heating (Gas) Oil/tonnes
781.6941

## Heat-Hot Water Profile
kWh | 159910 |  | Heating weeks per year | 8760 | Oil / Litres / Year | 0 | £ Oil / Year | 0
|  |  | Heating weeks per year | 0 | Cost of oil / Litre | 0 | Litres / Oil / Yr | 0
Month | kWh | Yearly % | Heating days per week | 0 | £ / Oil / Year | 0 | £ Oil / Litre | #DIV/0!
January | 21588 | 13.5% | Heating hours/ per day | 0 | kWh / Year | 0 | kWh / Year | 0
February | 22388 | 14% | Full Load Equivalent Hours
March | 15991 | 10% | 0 |  | Oil / Yr / £ | 0
April | 11194 | 7% | Load Factor % |  | Oil / litres / Year | 0
May | 6396 | 4% | 0% |  | Ave. Cost of Oil / litres | #DIV/0!
June | 4797 | 3% | School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
July | 4797 | 3% | Total kWh | 159910 | Heating Oil / litres | 0
August | 6396 | 4% | Monthly kWh | 0 | kWh | 0
September | 13593 | 8.5% | % of Total Cost | 0%
October | 15991 | 10% |  |  | kWh | 0
November | 17590 | 11% | Total kWh | 159910 | Heating Oil / litres | 0
December | 19189 | 12% | Montly kWh | 0
Totals | 159910 | 100% | % of Total Cost | 0%
kWh | 159912 |  | Heating weeks per year | 8760 | Oil / Litres / Year | 0 | £ Oil / Year | 0
|  |  | Heating weeks per year | 0 | Cost of oil / Litre | 0 | Litres / Oil / Yr | 0
Month | Yearly % | kWh | Heating days per week | 0 | £ / Oil / Year | 0 | £ Oil / Litre | #DIV/0!
January | 13.5% | 21588.12 | Heating hours/ per day | 0 | kWh / Year | 0 | kWh / Year | 0
February | 14% | 22387.68 | Full Load Equivalent Hours
March | 10% | 15991.2 | 0 |  | Oil / Yr / £ | 0
April | 7% | 11193.84 | Load Factor % |  | Oil / litres / Year | 0
May | 4% | 6396.48 | 0% |  | Ave. Cost of Oil / litres | #DIV/0!
June | 3% | 4797.36 | School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
July | 3% | 4797.36 | Total kWh | 159912 | Heating Oil / litres | 0
August | 4% | 6396.48 | Monthly kWh | 0 | kWh | 0
September | 8.5% | 13592.52 | % of Total Cost | 0%
October | 10% | 15991.2 |  |  | kWh | 0
November | 11% | 17590.32 | Total kWh | 159912 | Heating Oil / litres | 0
December | 12% | 19189.44 | Montly kWh | 0
| 100% | 159912 | % of Total Cost | 0%

## Woodchip Storage & Costs
© Biomass Wizard
Woodchip storage Calculator |  | Agricultual Building Calculator
Length / Metres | Width / Metres | Low Cost £300/m3
0 | 0 | m2 | Cost
Height | m3 | 0 | 0
0 | 0
Low Cost £430/m3
Length/m | Width/m | m2 | Cost
0 | 0 | 0 | 0
m2 | 0
Med Cost £580/m3
m2 | Height | m2 | Cost
0 | 0 | 0 | 0
m3 | 0
Cube & Square Root Calculator |  | High Cost £730/m3
m3 | Metres | m2 | Cost
0 | 0 | 0 | 0

## Conversion Tables (2)
Conversion Tables
Watts / m2 | 0 | FLEH | 0 |  | kWh /m2 | 0 | FLEH | 0
|  | kWh / m2 | 0 |  |  |  | Watts / m2 | #DIV/0!
Heating weeks per year |  | 8760 | FLEH |  | W/hr | 0 | MWh | 0
Heating weeks per year |  | 0 | 0 |  |  |  | kWh | 0
Heating days per week |  | 0 | Load Factor % |  |  |  | MJ | 0
Heating hours per heating day |  | 0 | 0% |  |  |  | BTU | 0
FLEH | 1400 | Annual Hours % | 15.98% |  | Annual Hours % | 15.98% | FLEH | 1399.848
kW | 0 | Power |  |  | kWh | 0 | Energy
FLEH | 0 | Ave. 2190 | FLEH = Full Load Equivalent Hours |  | FLEH | 0 | Ave. 2190 | FLEH = Full Load Equivalent Hours
kWh | 0 | Energy | Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%) |  | kW | #DIV/0! | Power | Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
kWh/kg | 0 | MJ | 0 |  | MJ | 0 | kWh/kg | 0
kWh | 0 | GWh | 0 |  | BTU | 0 | GWh | 0
|  | MWh | 0 |  |  |  | MWh | 0
|  | BTU | 0 |  |  |  | kWh | 0
|  | GJ | 0 |  |  |  | GJ | 0
|  | MJ | 0 |  |  |  | MJ | 0
|  | W | 0 |  |  |  | W | 0
MJ | 0 | MWh | 0 |  | GJ | 0 | MWh | 0
|  | kWh | 0 |  |  |  | kWh | 0
|  | GJ | 0 |  |  |  | MJ | 0
|  | BTU | 0 |  |  |  | BTU | 0
|  | W | 0 |  |  |  | W | 0
MWh | 0 | kWh | 0 |  | GWh | 0 | kWh | 0
|  | GWh | 0 |  |  |  | MWh | 0
|  | BTU | 0 |  |  |  | BTU | 0
|  | GJ | 0 |  |  |  | GJ | 0
ft | 0 | m | 0 |  | m | 0 | ft | 0
ft2 | 0 | m2 | 0 |  | m2 | 0 | ft2 | 0
Hoppus ft | 0 | m3 | 0 |  | m3 | 0 | Hoppus ft | 0
Acres | 0 | Ha | 0 |  | Ha | 0 | Acres | 0
°F | 0 | °C | -17.7778 |  |  |  | Heating Oil / L | 0
[7 empty] | kWh | 0
°C | 0 | °F | 32
Average room temp 21°C - 70°F | [6 empty] | kWh | 0
From | 0 | to | 0 | #DIV/0! |  |  | Heating Oil / L | 0
What is | 0 | of | 0 | #DIV/0! |  |  | Heating Oil / L | 0
[7 empty] | BTU | 0
Fraction | 0 | % | 0%
[7 empty] | BTU | 0
% | 0% | Fraction | 0 |  |  |  | Heating Oil / L | 0
Total | 0 | % | 0% | Saving | 0 | Sum | 0
Sum | 0 | % | 0% | Total | #DIV/0! | Saving | #DIV/0!
|  | % of Total | 31.96%
Total | 8760 |  |  | Cost | 2800 | Saving | 5960
|  | % Saving of Total | 68.04%

## Biomass - Size Requirements
Biomass heating of buildings of different sizes
Based on specific examples in the UK and elsewhere. These figures are given as guidance and precise energy requirements for a given building will depend on many construction and operational factors.
Building | System size (kW) | Full Load Equivalent Hours | Load Factor % | Primary energy kWh | Boiler Efficiency | Final outload kWh | CW Chips required |  | NCH Chips required |  | Wood Pellets required |  | Miscanthus Pellets required
[7 empty] | tonnes | m3 | tonnes | m3 | tonnes | m3 | tonnes | m3
| 0 | 0 | 0% | #DIV/0! | 0% | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
House x 3 beds | 15 | 2190 | 25% | 38647.0588 | 85% | 32850 | 11.0737 | 49.22 | 11.7112 | 35.93 | 8.2579 | 12.3807 | 8.862 | 13.2863
Farmhouse x 5 beds | 45 | 2190 | 25% | 115941.1765 | 85% | 98550 | 33.221 | 147.65 | 35.1337 | 107.78 | 24.7738 | 37.1421 | 26.5859 | 39.8589
House/Office/Cottage | 70 | 1752 | 20% | 144282.3529 | 85% | 122640 | 41.3416 | 183.75 | 43.7219 | 134.12 | 30.8296 | 46.2212 | 33.0847 | 49.6022
Small industrial unit | 120 | 1752 | 20% | 247341.1765 | 85% | 210240 | 70.8714 | 314.99 | 74.9519 | 229.92 | 52.8507 | 79.2364 | 56.7166 | 85.0324
Primary School | 180 | 1400 | 15.98% | 296470.5882 | 85% | 252000 | 84.9486 | 377.55 | 89.8396 | 275.59 | 63.3484 | 94.9751 | 67.9822 | 101.9224
Hotel | 250 | 2190 | 25% | 644117.6471 | 85% | 547500 | 184.5609 | 820.28 | 195.1872 | 598.74 | 137.632 | 206.3448 | 147.6995 | 221.4386
Country House/Swimming Pool/3 Cottages/Office | 300 | 2190 | 25% | 876000 | 75% | 657000 | 251.0029 | 1115.57 | 265.4545 | 814.28 | 187.1795 | 280.6289 | 200.8714 | 301.1565
High School | 550 | 1400 | 15.98% | 1026666.6667 | 75% | 770000 | 294.1738 | 1307.44 | 311.1111 | 954.33 | 219.3732 | 328.8954 | 235.42 | 352.9535
Municipal buildings | 700 | 1800 | 20.55% | 1680000 | 75% | 1260000 | 481.3754 | 2139.45 | 509.0909 | 1561.63 | 358.9744 | 538.1924 | 385.2327 | 577.5603
Large Commercial Greenhouse | 1500 | 1600 | 18.26% | 2823529.4118 | 85% | 2400000 | 809.0342 | 3595.71 | 855.615 | 2624.59 | 603.3183 | 904.5251 | 647.45 | 970.6896
District heating scheme | 4000 | 3000 | 34.25% | 16000000 | 75% | 12000000 | 4584.5272 | 20375.68 | 4848.4848 | 14872.66 | 3418.8034 | 5125.6423 | 3668.8833 | 5500.5746
Conifer Woodchip (CW) = 3,490 kWh/t - Non Coniferous Hardwood (NCH) = 3,300 kWh/t - Wood Pellets = 4,680 kWh/t - Miscanthus Pellets = 4,361 kWh/t
School = 1,400 Low = 1,752 (20%) Med = 2,190 (25%) High = 2,628 (30%) = 2,847 (32.5%)
Installation Type |  |  |  | kW Boiler Size | £ kW Installed |  | Approx Cost | Payback H/M/L
House x 3 beds |  |  |  | 15 | 1100 |  | 16500 | L
Farmhouse x 5 beds |  |  |  | 45 | 900 |  | 40500 | M
House / Office / Cottage |  |  |  | 70 | 900 |  | 63000 | M
Small industrial unit |  |  |  | 120 | 650 |  | 78000 | H
Primary School |  |  |  | 180 | 650 |  | 117000 | M
Hotel |  |  |  | 250 | 650 |  | 162500 | H
Country House / Swimming Pool / 3 Cottages / Office |  |  |  | 300 | 650 |  | 195000 | H
High School |  |  |  | 550 | 550 |  | 302500 | H
Municipal buildings |  |  |  | 700 | 550 |  | 385000 | H
Large Greenhouse |  |  |  | 1500 | 500 |  | 750000 | H
District heating scheme |  |  |  | 4000 | 500 |  | 2000000 | H
Figure 18 - From the Carbon Trust

## Flue Height
This spreadsheet is based on the Third Edition of the 1956 Clean Air Act Memorandum
[5 empty] | MW | 1
[5 empty] | million BTU/h | 0.293
[5 empty] | therm/h | 0.0293
[5 empty] | thousand BTU/s | 0.001055
MW
Calculation of Uncorrected Chimney Height for Very Low Sulphur Fuels
Heat input /kW |  | 120
MW |  | 0.12 | MW
Uncorrected stack height |  | 0.38111 | metre/s
Correction of chimney height for building effects
List the buildings within a distance of |  |  | 1.9055 | metre/s of the chimney
Include the any building to which the chimney is attached
Building | Height/Metres | Width/Metres | K | T
1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0
Corrected stack height |  | 0.38111 | metre/s
The final chimney height should be checked against the following requirements. If it does not satisfy them, it should be increased appropriately:
1. A chimney should terminate at least 3 m above the level of any adjacent area to which there is general access (i.e. ground level, roof areas or adjacent opening windows).
2. A chimney should never be less than the calculated uncorrected chimney height.
3. A chimney should never be less than the height of any part of an attached building within a distance of 5 times the uncorrected chimney height.
This spreadsheet is based on the Third Edition of the 1956 Clean Air Act Memorandum.
The spreadsheet is applicable in the following circumstances:
1. The sulphur content of the fuel is less than 0.04% by weight;
2. The gross heat input is in the range 0.15 MW (150 kW) to 150 MW;
3. The efflux velocity for the flue gas is adequate to prevent the plume flowing down the inside of the chimney:
For boilers up to 2.2 MW input the target velocity should not be less than 6 m/s at full load.
For boilers and similar plant rated up to 9 MW and equipped with induced draught fans, the velocity should not be less than 7.5 m/s at full load.
For boilers above 135 MW it should be 15 m/s.
For boilers between 9 MW and 135 MW, the efflux velocity should be estimated pro-rata between 7.5 m/s and 15 m/s.
4. Flue gases from more than one fuel burning plant in the same works should be discharged from a common chimney.
5. Flat terrain.
The spreadsheet does not apply to direct fired heating systems which discharge into the space being heated, gas turbines or incinerators.
The method does not take account of emissions of particulate matter.

## Emission-Fuel-Boiler Standards
© Biomass Wizard
Emissions - Fuel - Boiler Standards
Fuel | Plant Size | Pollution Control Regime | Regulator
Biomass fuel arising from natural sources | < 20 MWth | Clean Air Act | Local Authority
| 50 MWth < | IPPC | Environment Agency
| 20-50 MWth | LA-PPC | Local Authority
Waste or waste derived biomass, exempt from WID | <0.4-3 MWth and < 50 kg/hr | Clean Air Act | Local Authority
| 0.4 - 3 MWth and 50 - 1000 kg/hr | LA-PPC | Local Authority
| > 3 MWth and >1000 kg/hr | IPPC | Environment Agency
| 50 MWth < | IPPC | Environment Agency
Waste or waste derived biomass to which WID applied | < 3 MWth | WID, LA-IPPC | Local Authority
| 3 MWth < | WID, IPPC | Environment Agency
MW = megawatt, thermal.
LA-PPC = Local Authority Pollution Prevention and Control.
IPPC = Integrated Pollution Prevention and Control (Environment Agency).
WID = Waste Incineration Directive (Local Authority and Environment Agency)
Question | If yes | Action/Condition
Is it in a Smoke Control Area? | Is the proposed boiler on | Exexpt list boiler
the exempt list?
Is it in an Air Quality | Is your Environmental Health Officer (EHO) | Talk to EHO about conditions or refusal
Management Area? | concerned about NOx and PM10s?
Is the boiler over 400kW and using | Pollution Prevention Control Regulations | Talk to EHO about permit conditions.
a WID exempt waste wood? | 2000 will come into play.
Is the application lacking information on | Ask applicant for further details. | Condition for this to be undertaken by HETAS
who will install the system? |  | accredited installer with equipment manufacturer training.
Is there any information on | Ask for estimated delivery frequency | Possible condition on delivery
vehicle movements? | based on annual fuel usage and fuel type. | timings or maximum number.
Does delivery access look tight? | Ask who is supplying fuel and what | If access still looks tight then ask
| delivery vehicles will be used. | applicant to submit an alteration.
Do you want to impose a condition | Is it reasonable to ask for this | Set appropriate condition.
on fuel source? | immediately or at a later date?
Advice
If your boiler is regulated by the Environment Agency more information is available at:
http://www.environment-agency.gov.uk/business/topics/permitting/default.aspx]
Guidance on 'Biomass and Air Quality Information for Developers' follow this link to the Environmental Protection UK website:
www.environmental-protection.org.uk/assets/library/documents/Biomass_Developers_Leaflet.pdf
LACORS (Now LG Regulation) & Environmental Protection UK - Guidance for Local Authorities can be found at:
http://www.environmental-protection.org.uk/assets/library/documents/Biomass_and_Air_Quality_Guidance.pdf
Biomass boiler standard
BS EN 303-5:1999 applies to heating boilers for solid fuels, hand and automatically fired, nominal heat output of up to 300kW.
This standard covers properties such as performance, efficiency, emissions, thermal output, pressure testing, safety measures and testing.
Biomass boilers <300kw to meet the efficiency standards of EN303-5:1999.
Boilers >300kw should have an efficiency rating above 85%.
Fuel Standards
Woodfuel used in biomass boilers should meet recognised fuel quality standards in particular CEN/TS 14961:2005.
The characteristics of the fuel used in biomass boilers have an important influence on pollution emissions.
These include the origin of the fuel, chemical and physical properties.
The use of quality wood fuel benefits reductions in pollution emissions from biomass boilers.
This can be achieved through the use of wood that complies with biomass quality standards such as CEN/TC 335 and ONORM.
The fuel specifications and classes for all solid biofuels are set out in CEN/TS 14961:2005, which defines certain chemical and physical parameters and property classes.
Woodfuel used in biomass boilers to meet recognised fuel quality standards in particular CEN/TS 14961:2005.
Generally wood fuel of a consistent size and density is more favourable in terms of lower pollution emissions; wood pellets display these characteristics.
Fuel quality control must be considered to guarantee that a constant supply of good quality wood is delivered and used throughout the operation of biomass boiler.

## Hot Water
Hot Water Consumption
Type of building | Consumption per occupant | Peak demand per occupant | Storage per occupant
| litres / day | litres / hr | litres
Factories (no process) | 22 - 45 | 9 | 5
Hospitals, general | 160 | 30 | 27
Hospitals, mental | 110 | 22 | 27
Hostels | 90 | 45 | 30
Hotels | 90 - 160 | 45 | 30
Houses and flats | 90 - 160 | 45 | 30
Offices | 22 | 9 | 5
Schools, boarding | 115 | 20 | 25
Schools, day | 15 | 9 | 5
20 kWh per person / per day in the home

## Install Info
Planning & Building Regulations
Please ensure all relevant planning and building regulation requirements have been met
prior to commencement of installation.
Flue Requirements
An adequate flue system is vital to the operation of a biomass boiler. This should include
a draught stabiliser and explosion flap and meet requirements of the boiler to be installed.
Contact your boiler installer for information on specific flue requirements
for your biomass boiler.
It is assumed that all relevant planning and environmental approvals
(e.g. Clean Air Act, EPA, LAQM) will be obtained by the client prior to installation.
Electrical
An adequate electrical supply should be installed in the boiler room prior to commencement
of installation. Lighting and small power MUST also be available prior to
commencement of installation.
Water Supply and Drainage
A mains water supply (2bar min.) and drain will be required for pressurisation and safety
devices and must be available at commencement of installation.
Contact your boiler installer / supplier for further advice.
Fuel - Woodchip Boilers
Clean virgin timber at G30 and up to W30.
Fuel - Pellet Boilers
6 - 10mm Wood Pellets
Delivery
Delivery for equipment is usually 6 - 8 weeks from date of order.
Warranties on Equipment - This will vary between the various boilers/suppliers.
Warranty on electrical equipment is one year from commissioning.
Warranty on other moving parts is two years from commissioning.
Warranty on non-moving parts is three years from commissioning.